AuroraMONO Split 3D DC Inverter Air Conditioner

SERVICEMANUALMono 3D

z

Revision A: 160003001, Content updated.

Table of Contents

- Precaution

- Part Names And Functions

- Dimension

- Refrigerant Cycle Diagram

- Printed Circuit Board Connector Wiring Diagram of Outdoor unit

- Installation Details

- Operation Characteristics

- Electronic Function

- Troubleshooting

- Disassembly Instructions

WARNING

- Installation MUST conform with local building codes or, in the absence of local codes, with the National Electrical Code NFPA70/ANSI C1-1993 or current edition and Canadian Electrical Code Part1 CSA C.22.1.

- The information contained in the manual is intended for use by a qualified service technician familiar with safety procedures and equipped with the proper tools and test instruments

- Installation or repairs made by unqualified persons can result in hazards to you and others.

- Failure to carefully read and follow all instructions in this manual can result in equipment malfunction, property damage, personalinjury and/or death.

- This service is only for service engineer to use.

CONTENTS

1. Precaution	1

1.1 Safety Precaution	1

1.2 Warning	1

2. Part Names And Functions	4

2.1 Model Names of Indoor/Outdoor units	4

2.2 Part names of Indoor/Outdoor units	5

3. Dimension	6

3.1 Indoor Unit	6

3.2 Outdoor Unit	8

4. Refrigerant Cycle Diagram	10

5. Wiring Diagram	11

6 Installation Details	17

6.1 Wrench torque sheet for installation	17

6.2 Connecting the cables	17

6.3 Pipe length and the elevation	17

6.4 Installation for the first time	18

6.5 Adding the refrigerant after running the system for many years	19

6.6 Re-installation while the indoor unit need to be repaired	19

6.7 Re-installation while the outdoor unit need to be repaired	20

7. Operation Characteristics	22

8. Electronic Function	23

8.1 Abbreviation	23

8.2 Display function	23

8.3 Main Protection	24

8.4 Operation Modes and Functions	25

9. Troubleshooting	30

9.1 Indoor Unit Error Display	31

9.2 Outdoor unit error display	32

9.3 Diagnosis and Solution	38

10 Disassembly Instructions	63

10.1 Indoor unit	63

10.2 Outdoor unit	67

# 1. Precaution

## 1.1 Safety Precaution

To prevent injury to the user or other people and property damage, the following instructions must be followed.

Incorrect operation due to ignoring instruction will cause harm or damage.

Before service the unit, be sure to read this service manual at first.

## 1.2 Warning

Installation

Do not use a defective or underrated circuit breaker. Use this appliance on a dedicated circuit.

There is risk of fire or electric shock.

For electrical work, contact the dealer, seller, a qualified electrician, or an authorized service center.

Do not disassemble or repair the product, there is risk of fire or electric shock.

Always ground the product.

There is risk of fire or electric shock.

Install the panel and the cover of control box securely.

There is risk of fire of electric shock.

Always install a dedicated circuit and breaker.

Improper wiring or installation may cause  electric shock.

Use the correctly rated breaker of fuse.

There is risk of fire or electric shock.

Do not modify or extend the power cable.

There is risk of fire or electric shock.

Do not install, remove, or reinstall the unit by yourself(customer).

There is risk of fire, electric shock, explosion, or injury.

Be caution when unpacking and installing the product.

Sharp edges could cause injury, be especially careful of the case edges and the fins on the condenser and evaporator.

For installation, always contact the dealer or an authorized service center.

Do not install the product on a defective installation stand.

Be sure the installation area does not deteriorate with age.

If the base collapses, the air conditioner could fall with it, causing property damage, product failure, and personal injury.

Do not let the air conditioner run for a long time when the humidity is very high and a door or a window is left open.

Take care to ensure that power cable could not be pulled out or damaged during operation.

There is risk of fire or electric shock.

Do not place anything on the power cable.

There is risk of fire or electric shock.

Do not plug or unplug the power supply plug during operation.

There is risk of fire or electric shock.

Do not touch (operation) the product with wet hands.

Do not place a heater or other appliance near the power cable.

There is risk of fire and electric shock.

Do not allow water to run into electrical parts.

It may cause fire, failure of the product, or electric shock.

Do not store or use flammable gas or combustible near the product.

There is risk of fire or failure of product.

Do not use the product in a tightly closed space for a long time.

Oxygen deficiency could occur.

When flammable gas leaks, turn off the gas and open a window for ventilation before turn the product on.

If strange sounds or smoke comes from product,turn the breaker off or disconnect the power supply cable.

There is risk of electric shock or fire.

Stop operation and close the window in storm or hurricane. If possible, remove the product from the window before the hurricane arrives.

There is risk of property damage, failure of product, or electric shock.

Do not open the inlet grill of the product during operation. (Do not touch the electrostatic filter, if the unit is so equipped.)

There is risk of physical injury, electric shock, or product failure.

When the product is soaked, contact an authorized service center.

There is risk of fire or electric shock.

Be caution that water could not enter the product.

There is risk of fire, electric shock, or product damage.

Ventilate the product from time to time when operating it together with a stoveetc.

There is risk of fire or electric shock.

Turn the main power off when cleaning or maintaining the product.

There is risk of electric shock.

When the product is not be used for a long time, disconnect the power supply plug or turn off the breaker.

There is risk of product damage or failure, or unintended operation.

Take care to ensure that nobody could step on or fall onto the outdoor unit.

This could result in personal injury and product damage.

CAUTION

Always check for gas (refrigerant) leakage after installation or repair of product.

Low refrigerant levels may cause failure of product.

Install the drain hose to ensure that water is drained away properly.

A bad connection may cause water leakage.

Keep level even when installing the product.

It can avoid vibration of water leakage.

Do not install the product where the noise or hot air from the outdoor unit could damage the neighborhoods.

It may cause a problem for your neighbors.

Use two or more people to lift and transport the product.

Do not install the product where it will be exposed to sea wind (salt spray) directly.

It may cause corrosion on the product. Corrosion, particularly on the condenser and evaporator fins, could cause product malfunction or inefficient operation.

Operational

Do not expose the skin directly to cool air for long time. (Do not sit in the draft).

Do not use the product for special purposes, such as preserving foods, works of artetc. It is a consumer air conditioner, not a precision refrigerant system.

There is risk of damage or loss of property.

Do not block the inlet or outlet of air flow.

Use a soft cloth to clean. Do not use harsh detergents, solvents, etc.

There is risk of fire, electric shock, or damage to the plastic parts of the product.

Do not touch the metal parts of the product when removing the air filter. They are very sharp.

Do not step on or put anything on the product. (outdoor units)

Always insert the filter securely. Clean the filter every two weeks or more often if necessary.

A dirty filter reduces the efficiency of the air conditioner and could cause product malfunction or damage.

Do not insert hands or other objects through air inlet or outlet while the product is operated.

Do not drink the water drained from the product.

Use a firm stool or ladder when cleaning or maintaining the product.

Be careful and avoid personal injury.

Replace the all batteries in the remote control with new ones of the same type. Do not mix old and new batteries or different types of batteries.

There is risk of fire or explosion.

Do not recharge or disassemble the batteries. Do not dispose of batteries in a fire.

They may burn of explode.

If the liquid from the batteries gets onto your skin or clothes, wash it well with clean water. Do not use the remote of the batteries have leaked.

# 2. Part Names And Functions

## 2.1 Model Names of Indoor/Outdoor units

| Capacity | Voltage | Midea Indoor units | Midea Outdoor units |
| --- | --- | --- | --- |
| 9k | 115V | MSABA-09HRFN1-BQ0W | MOBA30-09HDN1-BQ0W |
| 12k | 115V | MSABB-12HRFN1-BQ0W | MOBA30-12HDN1-BQ0W |
| 9k | 208-230V | MSABA-09HRFN1-MQ0W | MOBA30-09HDN1-MQ0W |
| 12k | 208-230V | MSABB-12HRFN1-MQ0W | MOBA30-12HDN1-MQ0W |
| 18k | 208-230V | MSABD-18HRFN1-MQ0W | MOB30-18HDN1-MQ0W |
| 24k | 208-230V | MSABE-23HRFN1-MQ0W | MOCA30-23HDN1-MQ0W |
| 30k | 208-230V | MSABF-30HRFN1-MR0W | MOD30-30HFN1-MR0W |
| 36k | 208-230V | MSABF-36HRFN1-MP0W | MOD30-36HFN1-MP0W |
| 9k | 115V | MSABB-09HRFN1-BT0W | MOBA30-09HFN1-BT0W |
| 12k | 115V | MSABB-12HRFN1-BT0W | MOB30-12HFN1-BT0W |
| 9k | 208-230V | MSABB-09HRFN1-MT0W | MOBA30-09HFN1-MT0W |
| 12k | 208-230V | MSABB-12HRFN1-MT0W | MOB30-12HFN1-MT0W |
| 18k | 208-230V | MSABE-18HRFN1-MT0W | MOCA31-18HFN1-MT0W |
| 24k | 208-230V | MSABE-24HRFN1-MT0W | MOD31-24HFN1-MT0W |

## 2.2 Part names of Indoor/Outdoor units

# 3. Dimension

## 3.1 Indoor Unit

| Model | WxDxH (mm) | WxDxH (inch) | Mounted plate |
| --- | --- | --- | --- |
| MSABA-09HRFN1-BQ0W， MSABA-09HRFN1-MQ0W， | 722x187x290 | 28.43x7.36x11.42 | A |
| MSABB-12HRFN1-BQ0W， MSABB-12HRFN1-MQ0W， MSABB-09HRFN1-BT0W，MSABB-12HRFN1-BT0W MSABB-09HRFN1-MT0W MSABB-12HRFN1-MT0W | 802x189x297 | 31.57x7.44x11.69 | B |
| MSABD-18HRFN1-MQ0W | 965x215x319 | 37.99x8.46x12.56 | C |
| MSABE-23HRFN1-MQ0W MSABE-18HRFN1-MT0W MSABE-24HRFN1-MT0W | 1080x226x335 | 42.52x8.90x13.19 | D |
| MSABF-30HRFN1-MR0W，MSABF-36HRFN1-MP0W， | 1259x282x362 | 49.57x11.10x14.25 | E |

For Mounted plate A，

For Mounted plate B，

For Mounted plate C，

For Mounted plate D，

For Mounted plate E，

## 3.2 Outdoor Unit

Note:The above drawing is only for reference. Theappearanceof your units may be different.

| Model | W | D | H | W1 | A | B |
| --- | --- | --- | --- | --- | --- | --- |
| MOBA30-09HDN1-BQ0W MOBA30-12HDN1-BQ0W MOBA30-09HDN1-MQ0W MOBA30-12HDN1-MQ0W MOBA30-09HFN1-BT0W MOBA30-09HFN1-MT0W | 770(mm) | 300(mm) | 555(mm) | 823(mm) | 530(mm) | 290(mm) |
|  | 30.31(inch) | 11.81(inch) | 21.85(inch) | 32.40 (inch) | 20.87(inch) | 11.42 (inch) |
| MOB30-18HDN1-MQ0W MOB30-12HFN1-BT0W MOB30-12HFN1-MT0W | 800(mm) | 333(mm) | 554(mm) | 823(mm) | 530(mm) | 290(mm) |
|  | 31.50(inch) | 13.11(inch) | 21.81(inch) | 32.40 (inch) | 20.87 (inch) | 11.42(inch) |
| MOCA30-18HFN1-MT0W | 845(mm) | 363(mm) | 702(mm) | 874(mm) | 549(mm) | 325(mm) |
|  | 33.27(inch) | 14.29(inch) | 27.64(inch) | 34.41 (inch) | 21.61 (inch) | 12.80 (inch) |
| MOD30-30HFN1-MR0W MOD30-36HFN1-MP0W MOD30-24HFN1-MT0W | 946(mm) | 420(mm) | 810(mm) | 1030(mm) | 673(mm) | 403(mm) |
|  | 37.24(inch) | 16.54(inch) | 31.89(inch) | 40.55(inch) | 26.50(inch) | 15.87(inch) |

# 4. Refrigerant Cycle Diagram

MSABA-09HRFN1-BQ0W，MSABB-12HRFN1-BQ0W，MSABA-09HRFN1-MQ0W，MSABB-12HRFN1-MQ0W，MSABD-18HRFN1-MQ0W, MSABE-23HRFN1-MQ0W， MSABB-09HRFN1-BT0W，MSABB-12HRFN1-BT0W,

MSABB-09HRFN1-MT0W, MSABB-12HRFN1-MT0W, MSABE-18HRFN1-MT0W, MSABE-24HRFN1-MT0W,MSABF-30HRFN1-MR0W，MSABF-36HRFN1-MP0W，

# 5. Wiring Diagram

(Pls refer the wiring diagram on the unit)

# 6Installation Details

## 6.1 Wrench torque sheet for installation

| Outside diameter |  | Torque | Additional tightening torque |
| --- | --- | --- | --- |
| Ф6.35mm | 1/4in | 1500N.cm(153kgf.cm) | 1600N.cm(163kgf.cm) |
| Ф9.52mm | 3/8in | 2500N.cm(255kgf.cm) | 2600N.cm(265kgf.cm) |
| Ф12.7mm | 1/2in | 3500N.cm(357kgf.cm) | 3600N.cm(367kgf.cm) |
| Ф15.9mm | 5/8in | 4500N.cm(459kgf.cm) | 4700N.cm(479kgf.cm) |
| Ф19mm | 3/4in | 6500N.cm(663kgf.cm) | 6700N.cm(683kgf.cm) |

## 6.2 Connecting the cables

The power cord should be selected according

to the following specifications sheet.

| Appliance Amps | AWG Wire Size |
| --- | --- |
| 10 | 18 |
| 13 | 16 |
| 18 | 14 |
| 25 | 12 |
| 30 | 10 |

The cable size and the current of the fuse or

switch are determined by the maximum

current indicated on the nameplate which

located on the side panel of the unit. Please

refer to the nameplate before selecting the

cable, fuse and switch.

## 6.3 Pipe length and the elevation

| Models | Pipe size |  |
| --- | --- | --- |
|  | Gas | Liquid |
| 9K | 3/8in (Ф9.52mm) | 1/4in (Ф6.35mm) |
| 12K,18K | 1/2in (Ф12.7mm) | 1/4in (Ф6.35mm) |
| 24K,30K,36K | 5/8in (Ф15.9mm) | 3/8in (Ф9.52mm) |

| Models | Standard length | Max. Elevation | Max. Length A | Additional refrigerant |
| --- | --- | --- | --- | --- |
| 9K,12K | 7.5m (24.6ft) | 10m (32.8ft) | 25m (82.0ft) | 15g/m (0.16oz/ft) |
| 18K | 7.5m (24.6ft) | 20m (65.6ft) | 30m (98.4ft) | 15g/m (0.16oz/ft) |
| 24K | 7.5m (24.6ft) | 20m (65.6ft) | 30m (98.4ft) | 30g/m (0.32oz/ft) |
| 30K | 7.5m (24.6ft) | 25m (82.0ft) | 50m (164ft) | 30g/m (0.32oz/ft) |
| 36K | 7.5m (24.6ft) | 30m (82.0ft) | 65m (213ft) | 30g/m (0.32oz/ft) |

## 6.4Installation for the first time

Air and moisture in the refrigerant system have undesirable effects as below:

- Pressure in the system rises.

- Operating current rises.

- Cooling or heating efficiency drops.

- Moisture in the refrigerant circuit may freeze and block capillary tubing.

- Water may lead to corrosion of parts in the refrigerant system.

Therefore, the indoor units and the pipes between indoor and outdoor units must be leak tested and evacuated to remove gas and moisture from the system.

Gas leak check (Soap water method):

Apply soap water or a liquid neutral detergent on the indoor unit connections or outdoor unit connections by a soft brush to check for leakage of the connecting points of the piping. If bubbles come out, the pipes have leakage.

1. Air purging with vacuum pump

- Completely tighten the flare nuts of the indoor and outdoor units, confirm that both the 2-way and 3-way valves are set to the closed position.

- Connect the charge hose with the push pin of handle lo to the 3-way valves gas service port..

- Connect the charge hose of handle hi connection to the vacuum pump.

- Fully open the handle Lo of the manifold valve.

- Operate the vacuum pump to evacuate.

- Make evacuation for 30 minutes and check whether the compound meter indicates -0.1Mpa(14.5Psi). Ifthe meter does not indicate -0.1Mpa(14.5Psi) after pumping 30 minutes, it should be pumped 20 minutes more. If the pressure can’t achieve -0.1Mpa(14.5Psi) after pumping 50 minutes, please check if there are some leakage points.Fully close the handle Lo valve of the manifold valve and stop the operation of the vacuum pump. Confirm that the gauge needle does not move (approximately 5 minutes after turning off the vacuum pump).

- Turn the flare nut of the 3-way valves about45° counterclockwise for 6 or 7seconds after the gascoming out, then tighten the flare nut again. Make sure the pressure display in the pressure indicator is a little higher than the atmosphere pressure. Then remove the charge hose from the 3 way valve.

- Fully open the 2 way valve and 3 way valve

and securely tighten the cap of the 3 way valve.

2. Air purging by refrigerant

Procedure:

1). Confirm that both the 2-way and 3-way valves are set to the closed position.

2). Connect the charge set and a charging cylinder to the service port of the 3-way valve.

3). Air purging.

Open the valves on the charging cylinder and the charge set. Purge the air by loosening the flare nut on the 2-way valve approximately 45’ for 3 seconds then closing it for 1 minute; repeat 3 times.

After purging the air, use a torque wrench to tighten the flare nut on the 2-way valve.

4). Check the gas leakage.

Check the flare connections for gas leakage.

5). Discharge the refrigerant.

Close the valve on the charging cylinder and discharge the refrigerant by loosening the flare nut on the 2-way valve approximately 45’ until the gauge indicates 0.3Mpa(43.5Psi) to 0.5 Mpa(72.5Psi).

6). Disconnect the charge set and the charging cylinder, and set the 2-way and 3-way valves to the open position.

Be sure to use a hexagonal wrench to operate the valve stems.

7). Mount the valve stems nuts and the service port cap.

Be sure to use a torque wrench to tighten the service port cap to a torque 18N·m.

Be sure to check the gas leakage.

## 6.5 Adding the refrigerant after running the system for many years

Procedure

1). Connect the charge hose to the 3-way service port, open the 2-way valve and the 3-way valve.

Connect the charge hose to the valve at the bottom of the cylinder. If the refrigerant is R410A, make the cylinder bottom up to ensure liquid charge.

2). Purge the air from the charge hose.

Open the valve at the bottom of the cylinder and press the check valve on the charge set to purge the air (be careful of the liquid refrigerant).

3) Put the charging cylinder onto the electronic scale and record the weight.

4) Operate the air conditioner at the cooling mode.

5) Open the valves (Low side) on the charge set and charge the system with liquid refrigerant.

6).When the electronic scale displays the proper weight (refer to the gauge and the pressure of the low side), disconnect the charge hose from the 3-way valve’s service port immediately and turn off the air conditioner before disconnecting the hose.

7). Mount the valve stem caps and the service port

Use torque wrench to tighten the service port cap to a torque of 18N.m.

Be sure to check for gas leakage.

## 6.6 Re-installation while the indoor unit need to be repaired

1. Collecting the refrigerant into the outdoor unit

Procedure

1). Confirm that both the 2-way and 3-way valves are set to the opened position

Remove the valve stem caps and confirm that the valve stems are in the opened position.

Be sure to use a hexagonal wrench to operate the valve stems.

2). Connect the charge hose with the push pin of handle lo to the 3-way valves gas service port.

3). Air purging of the charge hose.

Open the handle Lo valve of the manifold valve slightly to purge air from the charge hose for 5 seconds and then close it quickly.

4). Set the 2-way valve to the close position.

5). Operate the air conditioner at the cooling cycle and stop it when the gauge indicates 0.1Mpa(14.5Psi).

6). Set the 3-way valve to the closed position immediately

Do this quickly so that the gauge ends up indicating 0.3Mpa(43.5Psi) to 0.5 Mpa(72.5Psi).

Disconnect the charge set, and tighten the 2-way and 3-way valve’s stem nuts.

Use a torque wrench to tighten the 3-way valves service port cap to a torque of 18N.m.

Be sure to check for gas leakage.

2. Air purging by the refrigerant

Procedure:

1). Confirm that both the 2-way and 3-way valves are set to the closed position.

2). Connect the charge set and a charging cylinder to the service port of the 3-way valve

Leave the valve on the charging cylinder closed.

3). Air purging.

Open the valves on the charging cylinder and the charge set. Purge the air by loosening the flare nut on the 2-way valve approximately 45’ for 3 seconds then closing it for 1 minute; repeat 3 times.

After purging the air, use a torque wrench to tighten the flare nut on the 2-way valve.

4). Check the gas leakage

Check the flare connections for gas leakage.

5). Discharge the refrigerant.

Close the valve on the charging cylinder and discharge the refrigerant by loosening the flare nut on the 2-way valve approximately 45’ until the gauge indicates 0.3Mpa(43.5Psi) to 0.5 Mpa(72.5Psi).

6). Disconnect the charge set and the charging cylinder, and set the 2-way and 3-way valves to the open position

Be sure to use a hexagonal wrench to operate the valve stems.

7). Mount the valve stems nuts and the service port cap

Be sure to use a torque wrench to tighten the service port cap to a torque 18N.m.

Be sure to check the gas leakage.

## 6.7Re-installation while the outdoor unit need to be repaired

1. Evacuation forthe whole system

Procedure:

1).Confirm that both the 2-way and 3-way valves are set to the opened position.

2). Connect the vacuum pump to 3-way valve’s service port.

3). Evacuation for approximately one hour. Confirm that the compound meter indicates -0.1Mpa(14.5Psi).

4). Close the valve (Low side) on the charge set, turn off the vacuum pump, and confirm that the gauge needle does not move (approximately 5 minutes after turning off the vacuum pump).

5). Disconnect the charge hose from the vacuum pump.

2. Refrigerant charging

Procedure:

1). Connect the charge hose to the charging cylinder, open the 2-way valve and the 3-way valve

Connectthe charge hose which you disconnected from the vacuum pump to the valve at the bottom of the cylinder. If the refrigerant is R410A, make the cylinder bottom up to ensure liquid charge.

2). Purge the air from the charge hose

Open the valve at the bottom of the cylinder and press the check valve on the charge set to purge the air (be careful of the liquid refrigerant).

3) Put the charging cylinder onto the electronic scale and record the weight.

4). Open the valves (Low side) on the charge set and charge the system with liquid refrigerant

If the system cannot be charge with the specified amount of refrigerant, or can be charged with a little at a time (approximately 150g each time) , operating the air conditioner in the cooling cycle; however, one time is not sufficient, wait approximately 1 minute and then repeat the procedure.

5).When the electronic scale displays the proper weight, disconnect the charge hose from the 3-way valve’s service port immediately

If the system has been charged with liquid refrigerant while operating the air conditioner, turn off the air conditioner before disconnecting the hose.

6). Mounted the valve stem caps and the service port. Use torque wrench to tighten the

service port cap to a torque of 18N.m. Be sure

to check for gas leakage.

# 7. Operation Characteristics

| Temperature Mode | Cooling operation | Heating operation | Drying operation |
| --- | --- | --- | --- |
| Room temperature | 17℃～32℃ (62℉～90℉) | 0℃～30℃ (32℉～86℉) | 10℃～32℃ (50℉～90℉) |
| Outdoor temperature (MSABA-09HRFN1-BQ0W，MSABB-12HRFN1-BQ0W，MSABA-09HRFN1-MQ0W，MSABB-12HRFN1-MQ0W，MSABD-18HRFN1-MQ0W, MSABE-23HRFN1-MQ0W) | 0°C～50°C (32°F～122°F) | -15°C～30°C (5°F～86°F) | 0°C～50°C (32°F～122°F) |
|  | -15°C～50°C (5°F～122°F) (need low ambient cooling function) |  |  |
| Outdoor temperature (MSABF-30HRFN1-MR0W，MSABF-36HRFN1-MP0W，MSABB-09HRFN1-BT0W，MSABB-12HRFN1-BT0W, MSABB-09HRFN1-MT0W, MSABB-12HRFN1-MT0W, MSABE-18HRFN1-MT0W, MSABE-24HRFN1-MT0W) | -25°C～50°C (-13°F～122°F) | -25°C～50°C (-13°F～122°F) | 0°C～50°C (32°F～122°F) |

ΔT(℉)=9ΔT(℃)5+32

CAUTION:

1. If the air conditioner is used beyond the above conditions, certain safety protection features may come into operation and cause the unit to operate abnormally.

2. The room relative humidity should be less than 80%. If the air conditioner operates beyond this figure, the surface of the air conditioner may attract condensation. Please set the vertical air flow louver to its maximum angle (vertically to the floor), and set HIGH fan mode.

3. The optimum performance will be achieved during this operating temperature zone.

# 8. Electronic Function

## 8.1 Abbreviation

T1:  Indoor room temperature

T2:  Coil temperature of evaporator

T3:  Coil temperature of condenser

T4:  Outdoor ambient temperature

T5:  Compressor discharge temperature

## 8.2 Display function

8.2.1 Icon explanation on indoor display board.

Digital display:

Displays the temperature settings when the air conditioner is operational.

Displays the room temperature in FAN mode.

Displays the self-diagnostic codes.

Dispalys ‘’ for three seconds when Timer ON, Fresh, Swing, Turbo or Silence feature is activated.

Dispalys ‘’ for three seconds when Fresh, Swing, Turbo or Silence feature is cancelled.

Dispalys ‘’ under deforsting operation.

Dispalys ‘’ when anti-cold air feature is activated under heating mode.

Dispalys ‘’ during self clean operation (if aplicable).

Dispalys ‘’ under 8℃ heating operation (if aplicable).

When ECO function(optional) is actived,the “” illuminates gradually one by one as

In one second interval.

NOTE:

A guide on using the infrared remote is not included in this literature package.

## 8.3 Main Protection

8.3.1 Three minutes delay at restart for compressor

1 minute delay for the 1st time stand-up and 3 minutes delay for others.

8.3.2 Temperature protection of compressor top

The unit will stop working when the compressor top temp. protector cut off, and will restart after the compressor top temp. protector restart.

8.3.3 Temperature protection of compressor discharge

Compressor discharge temp. T5>115℃ for 5s, compressor stops.

8.3.4 Fan speed is out of control

When indoor fan speed keeps too low (300RPM) for certain time, the unit will stop and the LED will display the failure

8.3.5 Inverter module protection

The Inverter module has a protection function about current, voltage and temperature. If these protections happen, the corresponding code will display on indoor unit and the unit will stop working.

8.3.6 Indoor fan delayed open function

When the unit starts up, the louver will be active immediately and the indoor fan will open 7s later.

If the unit runs in heating mode, the indoor fan will be also controlled by anti-cold wind function.

8.3.7 Compressor preheating functions

Preheating permitting condition:

When T4(outdoor ambient temperature)＜3°C,the preheating function will be activated.

8.3.8Sensor protection at open circuit and breaking disconnection.

When there’s only one temperature sensorin malfunction , the air conditioner will keep working but show the error code, in case of anyemergency use.

When there’s more than one temperature sensor in malfunction, the air conditioner will stop working.

## 8.4 Operation Modes and Functions

8.4.1 Fan mode

(1) Outdoor fan and compressor stop.

(2) Temperature setting function is disabled, and no setting temperature is displayed.

(3) Indoor fan can be set to high/med/low/auto.

(4) The louver operates same as in cooling mode.

(5) Auto fan:

8.4.2 Cooling Mode

8.4.2.1 Compressor running rules

When T1-Ts<ΔT -2℃, the compressor will stop,

when T1—Ts>ΔT -0.5℃，the compressor will be activated.

ΔT is the programmed parameter of temperature compensation.

When the AC run in mute mode, the compressor will run with low frequency.

When the current is more than setting value, the current protection function will be activated, and the compressor will stop.

8.4.2.2 Outdoor fan running rules

The outdoor unit will be run at different fan speed according to T4.

For different outdoor units, the fan speeds are different.

8.4.2.3 Indoor fan running rules

In cooling mode, indoor fan runs all the time and the speed can be selected as high, medium, low and auto.

The indoor fan is controlled as below:

The auto fan acts as below rules:

8.4.2.4 Condenser temperature protection

---TP3<T3< TP3+5, the compressor frequency will decrease to the lower level until to F1 and then runs at F1.If TP3-3<T3< TP3, the compressor will keep running at the current frequency.

---T3< TP3-3, the compressor will not limit the frequency and resume to the former frequency.

---T3> TP3+5 for 5 seconds, the compressor will stop until T3< TP3-3.

8.4.2.5 Evaporator temperature protection

When Evaporator temperature temp.is less than setting value, the compressor will stop.

8.4.3 Heating Mode

8.4.3.1 Compressor running rules

When T1-Ts>-ΔT, the compressor will stop,

when T1-TS<ΔT-1.5，the compressor will be on.

ΔT is the programmed parameter of temperature compensation.

When the AC run in mute mode, the compressor will run with low frequency.

When the current is more than setting value, the current protection function will be activated and the compressor will stop.

8.4.3.2 Outdoor fan running rules

The outdoor unit will be run at different fan speed according to T4.

For different outdoor units, the fan speeds are different.

8.4.3.3 Indoor fan running rules

When the compressor is on, the indoor fan can be set to high/med/low/auto. And the anti-cold wind function has the priority.

The indoor fan is controlled as below:

Auto fan action in heating mode:

8.4.3.4 Defrosting mode
AC will enter the defrosting mode according to the value of temp. of T3 and the value range of temp. change of T3 and also the compressor running time.

During the defrosting mode, the compressor keep running, indoor and outdoor motor will stop,  defrost lamp of the indoor unit will be lighted “.”Will be displayed.

If any one of the following items is satisfied, the defrosting will finish and the machine will turn to normal heating mode.

----T3 rises to be higher than TCDE1℃.

----T3 keeps to be higher than TCDE2℃ for 80 seconds.

----The machine has run for 15 minutes in defrosting mode.

8.4.3.5 Evaporator coil temperature protection

Off: Compressor stops.

Decrease: Decrease the running frequency to the lower level.

Hold: Keep the current frequency.

Resume: No limitation for frequency.

8.4.4 Auto-mode

This mode can be chosen with remote controller and the setting temperature can be changed between17°C~30°C

In auto mode, the machine will choose cooling, heating or fan-only mode according to ΔT (ΔT =T1-Ts).

| ΔT=T1-Ts | Running mode |
| --- | --- |
| ΔT＞2℃ | Cooling |
| -2≤ΔT≤2℃ | Fan-only |
| ΔT<-2℃ | Heating |

Indoor fan will run at auto fan of the relevant mode.

The louver operates same as in relevant mode.

If the machine switches mode between heating and cooling, the compressor will keep stopping for 15 minutes and then choose mode according to T1-Ts.

If the setting temperature is modified, the machine will choose running function again.

8.4.5 Drying mode

Indoor fan speed is fixed at breeze and can’t be changed. The louver angle is the same as in cooling mode.

All protections are active and the same as that in cooling mode.

8.4.6 Forced operation function

Forced cooling mode:

The compressor and outdoor fan keep running and the indoor fan runs at low speed. After running for 30 minutes, AC will turn to auto mode with 24℃ setting temperature.

Forced auto mode:

The action of forced auto mode is the same as normal auto mode with 24℃ setting temperature.

When AC receives signals,such as switch on,switch off, timer on,timer off, mode setting,fanspeed setting,sleeping mode setting,follow me setting, it will quit the forced operation.

8.4.7 Timer function

8.4.7.1 Timing range is 24 hours.

8.4.7.2 Timer on. The machine will turn on automatically when reaching the setting time.

8.4.7.3 Timer off. The machine will turn off automatically when reaching the setting time.

8.4.7.4 Timer on/off. The machine will turn on automatically when reaching the setting “on” time, and then turn off automatically when reaching the setting “off” time.

8.4.7.5 Timer off/on. The machine will turn off automatically when reaching the setting “off” time, and then turn on automatically when reaching the setting “on” time.

8.4.7.6 The timer function will not change the AC current operation mode. Suppose AC is off now, it will not start up firstly after setting the “timer off” function. And when reaching the setting time, the timer LED will be off and the AC running mode has not been changed.

8.4.7.7 The setting time is relative time.

8.4.7.8 The AC will quit the timer function when it has malfunction.

8.4.8 Economy function

8.4.8.1 The sleep function is available in cooling, heating or auto mode.

8.4.8.2. Operation process in sleep mode is as follow:

When cooling, the setting temperature rises 1℃ (be lower than 30℃) every one hour, 2 hours later the setting temperature stops rising and the indoor fan is fixed at low speed.

When heating, the setting temperature decreases 1℃ (be higher than 17℃) every one hour, 2 hours later the setting temperature stops rising and indoor fan is fixed at low speed. (Anti-cold wind function has the priority).

8.4.8.3 Operation time in sleep mode is 7 hours. After 7 hours the AC quits this mode and turns off.

8.4.8.4 Timer setting is available

8.4.9 Auto-Restart function

The indoor unit is equipped with auto-restart function, which is carried out through an auto-restart module. In case of a sudden power failure, the module memorizes the setting conditions before the power failure. The unit will resume the previous operation setting (not including swing function) automatically after 3 minutes when power returns.

If the memorization condition is forced cooling mode, the unit will run in cooling mode for 30 minutes and turn to auto mode as 24℃ setting temp.

If AC is off before power off and AC is required to start up now, the compressor will have 1 minute delay when power on. Other conditions,the compressor will have 3 minutes delay when restarts.

8.4.10 Refrigerant Leakage Detection

With this new technology, the display area will show “EC” when the outdoor unit detects refrigerant leakage. This function is only available in cooling mode.

8.4.11 Louver Position Memory Function

When starting the unit again after shutting down, its louver will restore to the angle originally set by the user, but the precondition is that the angle must be within the allowable range, if it exceeds, it will memorize the maximum angle of the louver. During operation, if the power fails or the end user shuts down the unit in the turbo mode, thelouver will restore to the default angle.

8.4.12 8℃ Heating(optional)

In heating operation, the preset temperature of the air conditioner can be as lower as 8℃, which keeps the room temperature steady at 8℃ and prevents household things freezing when the house is unoccupied for a long time in severe cold weather.

8.4.13 Self clean(optional)

For heat pump models which are provided with this function, after running in cooling or drying mode, if the user press “Self Clean” button on remote controller, firstly, indoor unit runs in fan only mode for a while, then low heat operation and finally runs in fan only again. This function can keep the inside of indoor unit dry and prevent breeding of mold.

8.4.14 Follow me (optional)

- If the indoor PCB receives the signal which

results from pressing the FOLLOW ME button onremote controller, the buzzer will emit a sound and this indicates the follow me function is initiated. But when the indoor PCB receives signal which sent from remote controller every 3 minutes, the buzzer will not respond. When the unit is running with follow me function, the PCB will control the unit according to the temperature from follow me signal, and the temperature collection function of room temperature sensor will be shielded, but the error detective function of room temperature sensor will be still valid.

- When the follow me function is available,

the PCB will control the unit according to the roomtemperature from the remote controller and the setting temperature.

- The PCB will take action to the mode

change information from remote controller signal, but itwill not affected by the setting temperature.

- When the unit is running with follow me

function, if the PCB doesn’t receive any signal fromremote controller for 7 minutes or pressing FOLLOW ME button again, the follow me function will be turned off automatically, and the temperature will control the unit according to the room temperature detected from its own room temperature sensor and setting temperature.

8.4.15Silence operation(optional)

Press the “silence” button on remote controller to initiate SILENCE function. When the Silence function is activated, the compressor running frequency will keep lower than F2 and the indoor unit will bring faint breeze, which will reduce the noise to the lowest level and create a quiet and comfortable room for you.

8.4.16Point check function

Press the LED DISPLAY or LED or MUTE button of the remote controller three times, and then press the AIR DIRECTION or SWING button three times in ten seconds, the buzzer will keep ring for two seconds. The air conditioner will enter into the information enquiry status. You can press the LED DISPLAY or AIR DIRECTION button to check the next or front item’s information.

When the AC enter the “information enquiry” status, it will display the code name in 2 seconds, the details are as follows.

| Enquiry information | Displaying code | Meaning |
| --- | --- | --- |
| T1 | T1 | T1 temp. |
| T2 | T2 | T2 temp. |
| T3 | T3 | T3 temp. |
| T4 | T4 | T4 temp. |
| T2B | Tb | T2B temp. |
| TP | TP | TP temp. |
| TH | TH | TH temp. |
| Targeted Frequency | FT | Targeted Frequency |
| Actual Frequency | Fr | Actual Frequency |
| Indoor fan speed | IF | Indoor fan speed |
| Outdoor fan speed | OF | Outdoor fan speed |
| EXV opening angle | LA | EXV opening angle |
| Compressor continuous running time | CT | Compressor continuous running time |
| Causes of compressor stop. | ST | Causes of compressor stop. |
| Reserve | A0 |  |
| Reserve | A1 |  |
| Reserve | 0 |  |
| Reserve | 1 |  |
| Reserve | 2 |  |
| Reserve | 3 |  |
| Reserve | 4 |  |
| Reserve | 5 |  |
| Reserve | 6 |  |
| Reserve | L |  |
| Reserve | A |  |
| Reserve | U |  |
| Reserve | T |  |

When the AC enter into the information enquiry status, it will display the code value in the next 25s, the details are as follows.

| Enquiry information | Display value | Meaning | Remark |
| --- | --- | --- | --- |
| T1,T2,T3,T4, T2B,TP,TH, Targeted Frequency, Actual Frequency | -1F,-1E,-1d,-1c,-1b,-1A | -25,-24,-23,-22,-21,-20 | 1. All the displaying temperature is actual value. 2. All the temperature is °C no matter what kind of remote controller is used. 3. T1,T2,T3,T4,T2B display range:-25~70, TP display range:-20~130. 4. Frequency display range: 0~159HZ. 5. If the actual value exceeds the range, it will display the maximum value or minimum value. |
|  | -19—99 | -19—99 |  |
|  | A0,A1,…A9 | 100,101,…109 |  |
|  | b0,b1,…b9 | 110,111,…119 |  |
|  | c0,c1,…c9 | 120,121,…129 |  |
|  | d0,d1,…d9 | 130,131,…139 |  |
|  | E0,E1,…E9 | 140,141,…149 |  |
|  | F0,F1,…F9 | 150,151,…159 |  |
| Indoor fan speed /Outdoor fan speed | 0 | OFF |  |
|  | 1,2,3,4 | Low speed, Medium speed, High speed, Turbo | For some big capacity motors. |
|  | 14-FF | Actual fan speed=Display value turns to decimal value and then multiply 10. The unit is RPM. | For some small capacity motors, display value is from 14-FF(hexadecimal), the corresponding fan speed range is from 200-2550RPM. |
| EXV opening angle | 0-FF | Actual EXV opening value=Display value turns to decimal value and then multiply 2. |  |
| Compressor continuous running time | 0-FF | 0-255 minutes | If the actual value exceeds the range, it will display the maximum value or minimum value. |
| Causes of compressor stop. | 0-99 | For the detailed meaning, please consult with engineer | Decimal display |
| Reserve | 0-FF |  |  |

# 9. Troubleshooting

Safety

Electricity power is still kept in capacitors even the power supply is shut off. Do not forget to discharge the electricity power in capacitor.

Electrolytic Capacitors

(HIGH VOLTAGE! CAUTION!)

For other models, please connect discharge resistance (approx.100Ω 40W) or soldering iron (plug) between +, - terminals of the electrolytic capacitor on the contrary side of the outdoor PCB.

Note: The picture above is only for reference. The plug of your side may be different.

## 9.1 Indoor Unit Error Display

| Operation lamp | Timer lamp | Display | LED STATUS |
| --- | --- | --- | --- |
| ☆ 1 time | X | E0 | Indoor unit EEPROM parameter error |
| ☆ 2 times | X | E1 | Indoor / outdoor units communication error |
| ☆3 times | X | E2 | Zero-crossing signal detection error |
| ☆4 times | X | E3 | Indoor fan speed has been out of control |
| ☆ 5 times | X | E4 | Indoor room temperature sensor T1 open circuit or short circuit |
| ☆ 6 times | X | E5 | Evaporator coil temperature sensor T2 open circuit or short circuit |
| ☆7 times | X | EC | Refrigerant leakage detection |
| ☆1 times | O | F0 | Overload current protection |
| ☆2 times | O | F1 | Outdoor ambient temperature sensor T4 open circuit or short circuit |
| ☆3 times | O | F2 | Condensercoil temperature sensor T3 open circuit or short circuit |
| ☆4 times | O | F3 | Compressor discharge temperature sensor T5 open circuit or short circuit |
| ☆5 times | O | F4 | Outdoor unit EEPROM parameter error |
| ☆6 times | O | F5 | Outdoor fan speed has been out of control |
| ☆1 times | ☆ | P0 | IPM malfunction or IGBT over-strong current protection |
| ☆2 times | ☆ | P1 | Over voltage or over low voltage protection |
| ☆3 times | ☆ | P2 | High temperature protection of compressor top diagnosis and solution(only for 9k,12k models) |
| ☆4 times | ☆ | P3* | Outdoor ambient temperature too low. |
| ☆5 times | ☆ | P4 | Inverter compressor drive error |
| ☆6 times | ☆ | P5 | Indoor units mode conflict (multi-zone ONLY) |

O（light）X（off）☆（flash）

*P3

1) In heating mode, when the outdoor temperature is lower than -25 for 1 hour, the indoor unit display error code P3.

2) If the OUTDOOR temperature is higher than -22c for 10 minutes and compressor stop for 1 hour OR outdoor temperature is higher than -5C for 10 minutes, then the unit will return to work.

9.2 Outdoor unit error display(TBD)

9.3 Diagnosis and Solution

9.3.1EEPROM parameter error diagnosis and solution(E0/F4)

| Error Code | E0/F4 |
| --- | --- |
| Malfunction decision conditions | Indoor or outdoor PCB main chip does not receive feedback from EEPROM chip. |
| Supposed causes | - Installation mistake - PCB faulty |

Trouble shooting:

EEPROM: a read-only memory whose contents can be erased and reprogrammed using a pulsed voltage. For the location of EEPROM chip, please refer to the below photos.

Outdoor PCB

Indoor PCB

Note: The two photos above are only for reference, it’s may be not same totally with the ones on your side.

9.3.2Indoor / outdoor unit’s communication diagnosis and solution(E1)

| Error Code | E1 |
| --- | --- |
| Malfunction decision conditions | Indoor unit does not receive the feedback from outdoor unit during 110 seconds and this condition happens four times continuously. |
| Supposed causes | - Wiring mistake - Indoor or outdoor PCB faulty |

Trouble shooting:

*

* Vs is the voltage between S and  N ( for  115V  2014 models)

*Vs is the voltage between 2 and  3 ( for 2015 models)

Remark:

Use a multimeter to test the resistance of the reactor which does not connect with capacitor.

The normal value should be around zero ohm. Otherwise, the reactor must have malfunction and need to be replaced.

Remark:

Use a multimeter to test the DC voltage between 2 port and 3 port of outdoor unit. The red pin of multimeter connects with 2 port while the black pin is for 3 port.

When AC is normal running, the voltage will move alternately between -50V to 50V.

If the outdoor unit has malfunction, the voltage will move alternately with positive value.

While if the indoor unit has malfunction, the voltage will be a certain value.

9.3.3Zero crossing detection error diagnosis and solution (E2)

| Error Code | E2 |
| --- | --- |
| Malfunction decision conditions | When PCB does not receive zero crossing signal feedback for 4 minutes or the zero crossing signal time interval is abnormal. |
| Supposed causes | - Connection mistake - PCB faulty |

Trouble shooting:

9.3.4 Fan speed has been out of control diagnosis and solution(E3)

| Error Code | E3 |
| --- | --- |
| Malfunction decision conditions | When indoor fan speed keeps too low (300RPM) for certain time, the unit will stop and the LED will display the failure. |
| Supposed causes | - Wiring mistake - Fan ass’y faulty - Fan motor faulty - PCB faulty |

Trouble shooting:

Index 1:

1:Indoor or Outdoor DC Fan Motor(control chip is in fan motor)

Power on and when the unit is in standby, measure the voltage of pin1-pin3, pin4-pin3 in fan motor connector. If the value of the voltage is not in the range showing in below table, the PCB must has problems and need to be replaced.

DC motor voltage input and output(voltage: 220-240V~)

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | Vs/Vm | 280V~380V |
| 2 | --- | --- | --- |
| 3 | Black | GND | 0V |
| 4 | White | Vcc | 14-17.5V |
| 5 | Yellow | Vsp | 0~5.6V |
| 6 | Blue | FG | 14-17.5V |

DC motor voltage input and output(voltage :115V~)

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | Vs/Vm | 140V~190V |
| 2 | --- | --- | --- |
| 3 | Black | GND | 0V |
| 4 | White | Vcc | 14-17.5V |
| 5 | Yellow | Vsp | 0~5.6V |
| 6 | Blue | FG | 14-17.5V |

2.OutdoorDC Fan Motor (control chip is in outdoor PCB)

Power on ,and check if the fan can run normally, if the fan can run normally, the PCB must has problems and need to be replaced, If the fan can’t run normally, measure the resistance of each two pins. If the resistance is not equal to each other, the fan motor must have problems and need to be replaced, otherwise the PCB must has problems and need to be replaced.

3. Indoor AC Fan Motor

Power on and set the unit running in fan mode at high fan speed. After running for 15 seconds, measure the voltage of pin1 and pin2. If the value of the voltage is less than 100V(208~240V power supply)or 50V(115V power supply), the PCB must has problems and need to be replaced.

9.3.5Open circuit or short circuit of temperature sensor diagnosis and solution(E5)

| Error Code | E4/E5/F1/F2/F3 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is lower than 0.06V or higher than 4.94V, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Sensor faulty - PCB faulty |

Trouble shooting:

9.3.6Refrigerant Leakage Detection diagnosis and solution(EC)

| Error Code | EC |
| --- | --- |
| Malfunction decision conditions | Define the evaporator coil temp.T2 of the compressor just starts running as Tcool. In the beginning 5 minutes after the compressor starts up, if T2 ＜Tcool－2°C(Tcool－35.6°F) does not keep continuous 4 seconds and this situation happens 3 times, the display area will show “EC” and AC will turn off. |
| Supposed causes | - T2 sensor faulty - Indoor PCB faulty - System problems, such as leakage or blocking. |

Trouble shooting:

9.3.6 Overload current protection diagnosis and solution(F0)

| Error Code | F0 |
| --- | --- |
| Malfunction decision conditions | An abnormal current rise is detected by checking the specified current detection circuit. |
| Supposed causes | - Power supply problems. - System blockage - PCB faulty - Wiring mistake - Compressor malfunction |

9.3.7 IPM malfunction or IGBT over-strong current protection diagnosis and solution(P0)

| Error Code | P0 |
| --- | --- |
| Malfunction decision conditions | When the voltage signal that IPM send to compressor drive chip is abnormal, the display LED will show “P0” and AC will turn off. |
| Supposed causes | - Wiring mistake - IPM malfunction - Outdoor fan ass’y faulty - Compressor malfunction - Outdoor PCB faulty |

Trouble shooting:

For example:

Note: The photos below are only for reference, it’s may be not same totally with the ones on your side.

P-U

P-V

P-W

N-U

N-V

N-W

9.3.8Over voltage or too low voltage protection diagnosis and solution(P1)

| Error Code | P1 |
| --- | --- |
| Malfunction decision conditions | An abnormal voltage rise or drop is detected by checking the specified voltage detection circuit. |
| Supposed causes | - Power supply problems. - System leakage or block - PCB faulty |

Trouble shooting:

Remark:

Measure the DC voltage between P and N port. The normal value should be around 310V.

P

N

9.3.9 High temperature protection of compressor top diagnosis and solution(P2)

| Error Code | P2 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is not 5V, the LED will display the failure. |
| Supposed causes | - Power supply problems. - System leakage or block - PCB faulty |

Trouble shooting:

9.3.10 Inverter compressor drive error diagnosis and solution(P4)

| Error Code | P4 |
| --- | --- |
| Malfunction decision conditions | An abnormal inverter compressor drive is detected by a special detection circuit, including communication signal detection, voltage detection, compressor rotation speed signal detection and so on. |
| Supposed causes | - Wiring mistake - IPM malfunction - Outdoor fan ass’y faulty - Compressor malfunction - Outdoor PCB faulty |

Trouble shooting:

Main parts check

  - Temperature sensor checking

Disconnect the temperature sensor from PCB, measure the resistance value with a tester.

Temperature sensors.

Room temp.(T1) sensor,

Indoor coil temp.(T2) sensor,

Outdoor coil temp.(T3) sensor,

Outdoor ambient temp.(T4) sensor,

Compressor discharge temp.(T5) sensor.

Measure the resistance value of each winding by using the multi-meter.

Appendix 1 Temperature Sensor Resistance Value Table for T1,T2,T3,T4 (°C--K)

| °C | °F | K Ohm | °C | °F | K Ohm | °C | °F | K Ohm | °C | °F | K Ohm |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -20 | -4 | 115.266 | 20 | 68 | 12.6431 | 60 | 140 | 2.35774 | 100 | 212 | 0.62973 |
| -19 | -2 | 108.146 | 21 | 70 | 12.0561 | 61 | 142 | 2.27249 | 101 | 214 | 0.61148 |
| -18 | 0 | 101.517 | 22 | 72 | 11.5 | 62 | 144 | 2.19073 | 102 | 216 | 0.59386 |
| -17 | 1 | 96.3423 | 23 | 73 | 10.9731 | 63 | 145 | 2.11241 | 103 | 217 | 0.57683 |
| -16 | 3 | 89.5865 | 24 | 75 | 10.4736 | 64 | 147 | 2.03732 | 104 | 219 | 0.56038 |
| -15 | 5 | 84.219 | 25 | 77 | 10 | 65 | 149 | 1.96532 | 105 | 221 | 0.54448 |
| -14 | 7 | 79.311 | 26 | 79 | 9.55074 | 66 | 151 | 1.89627 | 106 | 223 | 0.52912 |
| -13 | 9 | 74.536 | 27 | 81 | 9.12445 | 67 | 153 | 1.83003 | 107 | 225 | 0.51426 |
| -12 | 10 | 70.1698 | 28 | 82 | 8.71983 | 68 | 154 | 1.76647 | 108 | 226 | 0.49989 |
| -11 | 12 | 66.0898 | 29 | 84 | 8.33566 | 69 | 156 | 1.70547 | 109 | 228 | 0.486 |
| -10 | 14 | 62.2756 | 30 | 86 | 7.97078 | 70 | 158 | 1.64691 | 110 | 230 | 0.47256 |
| -9 | 16 | 58.7079 | 31 | 88 | 7.62411 | 71 | 160 | 1.59068 | 111 | 232 | 0.45957 |
| -8 | 18 | 56.3694 | 32 | 90 | 7.29464 | 72 | 162 | 1.53668 | 112 | 234 | 0.44699 |
| -7 | 19 | 52.2438 | 33 | 91 | 6.98142 | 73 | 163 | 1.48481 | 113 | 235 | 0.43482 |
| -6 | 21 | 49.3161 | 34 | 93 | 6.68355 | 74 | 165 | 1.43498 | 114 | 237 | 0.42304 |
| -5 | 23 | 46.5725 | 35 | 95 | 6.40021 | 75 | 167 | 1.38703 | 115 | 239 | 0.41164 |
| -4 | 25 | 44 | 36 | 97 | 6.13059 | 76 | 169 | 1.34105 | 116 | 241 | 0.4006 |
| -3 | 27 | 41.5878 | 37 | 99 | 5.87359 | 77 | 171 | 1.29078 | 117 | 243 | 0.38991 |
| -2 | 28 | 39.8239 | 38 | 100 | 5.62961 | 78 | 172 | 1.25423 | 118 | 244 | 0.37956 |
| -1 | 30 | 37.1988 | 39 | 102 | 5.39689 | 79 | 174 | 1.2133 | 119 | 246 | 0.36954 |
| 0 | 32 | 35.2024 | 40 | 104 | 5.17519 | 80 | 176 | 1.17393 | 120 | 248 | 0.35982 |
| 1 | 34 | 33.3269 | 41 | 106 | 4.96392 | 81 | 178 | 1.13604 | 121 | 250 | 0.35042 |
| 2 | 36 | 31.5635 | 42 | 108 | 4.76253 | 82 | 180 | 1.09958 | 122 | 252 | 0.3413 |
| 3 | 37 | 29.9058 | 43 | 109 | 4.5705 | 83 | 181 | 1.06448 | 123 | 253 | 0.33246 |
| 4 | 39 | 28.3459 | 44 | 111 | 4.38736 | 84 | 183 | 1.03069 | 124 | 255 | 0.3239 |
| 5 | 41 | 26.8778 | 45 | 113 | 4.21263 | 85 | 185 | 0.99815 | 125 | 257 | 0.31559 |
| 6 | 43 | 25.4954 | 46 | 115 | 4.04589 | 86 | 187 | 0.96681 | 126 | 259 | 0.30754 |
| 7 | 45 | 24.1932 | 47 | 117 | 3.88673 | 87 | 189 | 0.93662 | 127 | 261 | 0.29974 |
| 8 | 46 | 22.5662 | 48 | 118 | 3.73476 | 88 | 190 | 0.90753 | 128 | 262 | 0.29216 |
| 9 | 48 | 21.8094 | 49 | 120 | 3.58962 | 89 | 192 | 0.8795 | 129 | 264 | 0.28482 |
| 10 | 50 | 20.7184 | 50 | 122 | 3.45097 | 90 | 194 | 0.85248 | 130 | 266 | 0.2777 |
| 11 | 52 | 19.6891 | 51 | 124 | 3.31847 | 91 | 196 | 0.82643 | 131 | 268 | 0.27078 |
| 12 | 54 | 18.7177 | 52 | 126 | 3.19183 | 92 | 198 | 0.80132 | 132 | 270 | 0.26408 |
| 13 | 55 | 17.8005 | 53 | 127 | 3.07075 | 93 | 199 | 0.77709 | 133 | 271 | 0.25757 |
| 14 | 57 | 16.9341 | 54 | 129 | 2.95896 | 94 | 201 | 0.75373 | 134 | 273 | 0.25125 |
| 15 | 59 | 16.1156 | 55 | 131 | 2.84421 | 95 | 203 | 0.73119 | 135 | 275 | 0.24512 |
| 16 | 61 | 15.3418 | 56 | 133 | 2.73823 | 96 | 205 | 0.70944 | 136 | 277 | 0.23916 |
| 17 | 63 | 14.6181 | 57 | 135 | 2.63682 | 97 | 207 | 0.68844 | 137 | 279 | 0.23338 |
| 18 | 64 | 13.918 | 58 | 136 | 2.53973 | 98 | 208 | 0.66818 | 138 | 280 | 0.22776 |
| 19 | 66 | 13.2631 | 59 | 138 | 2.44677 | 99 | 210 | 0.64862 | 139 | 282 | 0.22231 |

Appendix 2Temperature Sensor Resistance Value Table for T5 (°C --K)

| °C | °F | K Ohm | °C | °F | K Ohm | °C | °F | K Ohm | °C | °F | K Ohm |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -20 | -4 | 542.7 | 20 | 68 | 68.66 | 60 | 140 | 13.59 | 100 | 212 | 3.702 |
| -19 | -2 | 511.9 | 21 | 70 | 65.62 | 61 | 142 | 13.11 | 101 | 214 | 3.595 |
| -18 | 0 | 483 | 22 | 72 | 62.73 | 62 | 144 | 12.65 | 102 | 216 | 3.492 |
| -17 | 1 | 455.9 | 23 | 73 | 59.98 | 63 | 145 | 12.21 | 103 | 217 | 3.392 |
| -16 | 3 | 430.5 | 24 | 75 | 57.37 | 64 | 147 | 11.79 | 104 | 219 | 3.296 |
| -15 | 5 | 406.7 | 25 | 77 | 54.89 | 65 | 149 | 11.38 | 105 | 221 | 3.203 |
| -14 | 7 | 384.3 | 26 | 79 | 52.53 | 66 | 151 | 10.99 | 106 | 223 | 3.113 |
| -13 | 9 | 363.3 | 27 | 81 | 50.28 | 67 | 153 | 10.61 | 107 | 225 | 3.025 |
| -12 | 10 | 343.6 | 28 | 82 | 48.14 | 68 | 154 | 10.25 | 108 | 226 | 2.941 |
| -11 | 12 | 325.1 | 29 | 84 | 46.11 | 69 | 156 | 9.902 | 109 | 228 | 2.86 |
| -10 | 14 | 307.7 | 30 | 86 | 44.17 | 70 | 158 | 9.569 | 110 | 230 | 2.781 |
| -9 | 16 | 291.3 | 31 | 88 | 42.33 | 71 | 160 | 9.248 | 111 | 232 | 2.704 |
| -8 | 18 | 275.9 | 32 | 90 | 40.57 | 72 | 162 | 8.94 | 112 | 234 | 2.63 |
| -7 | 19 | 261.4 | 33 | 91 | 38.89 | 73 | 163 | 8.643 | 113 | 235 | 2.559 |
| -6 | 21 | 247.8 | 34 | 93 | 37.3 | 74 | 165 | 8.358 | 114 | 237 | 2.489 |
| -5 | 23 | 234.9 | 35 | 95 | 35.78 | 75 | 167 | 8.084 | 115 | 239 | 2.422 |
| -4 | 25 | 222.8 | 36 | 97 | 34.32 | 76 | 169 | 7.82 | 116 | 241 | 2.357 |
| -3 | 27 | 211.4 | 37 | 99 | 32.94 | 77 | 171 | 7.566 | 117 | 243 | 2.294 |
| -2 | 28 | 200.7 | 38 | 100 | 31.62 | 78 | 172 | 7.321 | 118 | 244 | 2.233 |
| -1 | 30 | 190.5 | 39 | 102 | 30.36 | 79 | 174 | 7.086 | 119 | 246 | 2.174 |
| 0 | 32 | 180.9 | 40 | 104 | 29.15 | 80 | 176 | 6.859 | 120 | 248 | 2.117 |
| 1 | 34 | 171.9 | 41 | 106 | 28 | 81 | 178 | 6.641 | 121 | 250 | 2.061 |
| 2 | 36 | 163.3 | 42 | 108 | 26.9 | 82 | 180 | 6.43 | 122 | 252 | 2.007 |
| 3 | 37 | 155.2 | 43 | 109 | 25.86 | 83 | 181 | 6.228 | 123 | 253 | 1.955 |
| 4 | 39 | 147.6 | 44 | 111 | 24.85 | 84 | 183 | 6.033 | 124 | 255 | 1.905 |
| 5 | 41 | 140.4 | 45 | 113 | 23.89 | 85 | 185 | 5.844 | 125 | 257 | 1.856 |
| 6 | 43 | 133.5 | 46 | 115 | 22.89 | 86 | 187 | 5.663 | 126 | 259 | 1.808 |
| 7 | 45 | 127.1 | 47 | 117 | 22.1 | 87 | 189 | 5.488 | 127 | 261 | 1.762 |
| 8 | 46 | 121 | 48 | 118 | 21.26 | 88 | 190 | 5.32 | 128 | 262 | 1.717 |
| 9 | 48 | 115.2 | 49 | 120 | 20.46 | 89 | 192 | 5.157 | 129 | 264 | 1.674 |
| 10 | 50 | 109.8 | 50 | 122 | 19.69 | 90 | 194 | 5 | 130 | 266 | 1.632 |
| 11 | 52 | 104.6 | 51 | 124 | 18.96 | 91 | 196 | 4.849 |  |  |  |
| 12 | 54 | 99.69 | 52 | 126 | 18.26 | 92 | 198 | 4.703 |  |  |  |
| 13 | 55 | 95.05 | 53 | 127 | 17.58 | 93 | 199 | 4.562 |  |  |  |
| 14 | 57 | 90.66 | 54 | 129 | 16.94 | 94 | 201 | 4.426 |  |  |  |
| 15 | 59 | 86.49 | 55 | 131 | 16.32 | 95 | 203 | 4.294 |  |  |  |
| 16 | 61 | 82.54 | 56 | 133 | 15.73 | 96 | 205 | 4.167 |  |  |  |
| 17 | 63 | 78.79 | 57 | 135 | 15.16 | 97 | 207 | 4.045 |  |  |  |
| 18 | 64 | 75.24 | 58 | 136 | 14.62 | 98 | 208 | 3.927 |  |  |  |
| 19 | 66 | 71.86 | 59 | 138 | 14.09 | 99 | 210 | 3.812 |  |  |  |

Appendix 3:

ΔT(℉)=9ΔT(℃)5

| °C | °F | °C | °F | °C | °F | °C | °F | °C | °F |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -5 | 23 | 21 | 69.8 | 51 | 123.8 | 82 | 179.6 | 113 | 235.4 |
| -4 | 24.8 | 22 | 71.6 | 52 | 125.6 | 83 | 181.4 | 114 | 237.2 |
| -3 | 26.6 | 23 | 73.4 | 53 | 127.4 | 84 | 183.2 | 115 | 239 |
| -2 | 28.4 | 24 | 75.2 | 54 | 129.2 | 85 | 185 | 116 | 240.8 |
| -1 | 30.2 | 25 | 77 | 55 | 131 | 86 | 186.8 | 117 | 242.6 |
| 0 | 32 | 25.5 | 77.9 | 56 | 132.8 | 87 | 188.6 | 118 | 244.4 |
| 0.5 | 32.9 | 26 | 78.8 | 57 | 134.6 | 88 | 190.4 | 119 | 246.2 |
| 1 | 33.8 | 27 | 80.6 | 58 | 136.4 | 89 | 192.2 | 120 | 248 |
| 1.5 | 34.7 | 28 | 82.4 | 59 | 138.2 | 90 | 194 | 121 | 249.8 |
| 2 | 35.6 | 29 | 84.2 | 60 | 140 | 91 | 195.8 | 122 | 251.6 |
| 2.5 | 36.5 | 30 | 86 | 61 | 141.8 | 92 | 197.6 | 123 | 253.4 |
| 3 | 37.4 | 31 | 87.8 | 62 | 143.6 | 93 | 199.4 | 124 | 255.2 |
| 3.5 | 38.3 | 32 | 89.6 | 63 | 145.4 | 94 | 201.2 | 125 | 257 |
| 4 | 39.2 | 33 | 91.4 | 64 | 147.2 | 95 | 203 | 126 | 258.8 |
| 4.5 | 40.1 | 34 | 93.2 | 65 | 149 | 96 | 204.8 | 127 | 260.6 |
| 5 | 41 | 35 | 95 | 66 | 150.8 | 97 | 206.6 | 128 | 262.4 |
| 6 | 42.8 | 36 | 96.8 | 67 | 152.6 | 98 | 208.4 | 129 | 264.2 |
| 7 | 44.6 | 37 | 98.6 | 68 | 154.4 | 99 | 210.2 | 130 | 266 |
| 8 | 46.4 | 38 | 100.4 | 69 | 156.2 | 100 | 212 | 131 | 267.8 |
| 9 | 48.2 | 39 | 102.2 | 70 | 158 | 101 | 213.8 | 132 | 269.6 |
| 10 | 50 | 40 | 104 | 71 | 159.8 | 102 | 215.6 | 133 | 271.4 |
| 11 | 51.8 | 41 | 105.8 | 72 | 161.6 | 103 | 217.4 | 134 | 273.2 |
| 12 | 53.6 | 42 | 107.6 | 73 | 163.4 | 104 | 219.2 | 135 | 275 |
| 13 | 55.4 | 43 | 109.4 | 74 | 165.2 | 105 | 221 | 136 | 276.8 |
| 14 | 57.2 | 44 | 111.2 | 75 | 167 | 106 | 222.8 | 137 | 278.6 |
| 15 | 59 | 45 | 113 | 76 | 168.8 | 107 | 224.6 | 138 | 280.4 |
| 16 | 60.8 | 46 | 114.8 | 77 | 170.6 | 108 | 226.4 | 139 | 282.2 |
| 17 | 62.6 | 47 | 116.6 | 78 | 172.4 | 109 | 228.2 | 140 | 284 |
| 18 | 64.4 | 48 | 118.4 | 79 | 174.2 | 110 | 230 | 141 | 285.8 |
| 19 | 66.2 | 49 | 120.2 | 80 | 176 | 111 | 231.8 | 142 | 287.6 |
| 20 | 68 | 50 | 122 | 81 | 177.8 | 112 | 233.6 | 143 | 289.4 |

2.Compressor checking

Measure the resistance value of each winding by using the tester.

| Position | Resistance Value |  |  |  |
| --- | --- | --- | --- | --- |
|  | ASN98D22UFZ | ASM135D23UFZ | ATF235D22UMT | ATF250D22UMT |
| Blue - Red | 1.57Ω | 1.75 Ω | 0.75 Ω | 0.75 Ω |
| Blue - Black |  |  |  |  |
| Red - Blue |  |  |  |  |

3.IPM continuity check

Turn off the power, let the large capacity electrolytic capacitors discharge completely, and dismount the IPM. Use a digital tester to measure the resistance between P and UVWN; UVW and N.

| Digital tester |  | Normal resistance value | Digital tester |  | Normal resistance value |
| --- | --- | --- | --- | --- | --- |
| (+)Red | (-)Black | ∞ (Several MΩ) | (+)Red | (-)Black | ∞ (Several MΩ) |
| P | N |  | U | N |  |
|  | U |  | V |  |  |
|  | V |  | W |  |  |
|  | W |  | (+)Red |  |  |

4: Indoor outdoor Fan Motor

Measure the resistance value of each winding by using the tester.

| Model |  | YKT-32-6-202L | YKT-32-6-3L | YKT-48-6-206 | YKT-63-6-200L |
| --- | --- | --- | --- | --- | --- |
| Brand |  | Tongde | Welling | Welling | Welling |
| Black – Red Main | Ω | 86 | 213 | 152 | 88.5 |
| Blue –Black AUX | Ω | 64 | 156 | 142 | 138 |

5:Pressure On Service Port

Cooling chart:

| °F(°C) | ODT IDT | 75 (23.89) | 85 (29.44) | 95 (35) | 105 (40.56) | 115 (46.11) |
| --- | --- | --- | --- | --- | --- | --- |
| BAR | 70/59 | 8.2 | 7.8 | 8.1 | 8.6 | 10.1 |
| BAR | 75/63 | 8.6 | 8.3 | 8.7 | 9.1 | 10.7 |
| BAR | 80/67 | 9.3 | 8.9 | 9.1 | 9.6 | 11.2 |
| °F(°C) | ODT IDT | 75 (23.89) | 85 (29.44) | 95 (35) | 105 (40.56) | 115 (46.11) |
| PSI | 70/59 | 119 | 113 | 117 | 125 | 147 |
| PSI | 75/63 | 124 | 120 | 126 | 132 | 155 |
| PSI | 80/67 | 135 | 129 | 132 | 140 | 162 |
| °F(°C) | ODT IDT | 75 (23.89) | 85 (29.44) | 95 (35) | 105 (40.56) | 115 (46.11) |
| MPA | 70/59 | 0.82 | 0.78 | 0.81 | 0.86 | 1.01 |
| MPA | 75/63 | 0.86 | 0.83 | 0.87 | 0.91 | 1.07 |
| MPA | 80/67 | 0.93 | 0.89 | 0.91 | 0.96 | 1.12 |

Heating Chart:

| °F(°C) | ODT IDT | 57/53 (13.89/11.67) | 47/43 (8.33/6.11) | 37/33 (2.78/0.56) | 27/23 (-2.78/-5) | 17/13 (-8.33/-10.56) |
| --- | --- | --- | --- | --- | --- | --- |
| BAR | 55 | 30.3 | 28.5 | 25.3 | 22.8 | 20.8 |
| BAR | 65 | 32.5 | 30.0 | 26.6 | 25.4 | 23.3 |
| BAR | 75 | 33.8 | 31.5 | 27.8 | 26.3 | 24.9 |
| °F (°C) | ODT IDT | 57/53 (13.89/11.67) | 47/43 (8.33/6.11) | 37/33 (2.78/0.56) | 27/23 (-2.78/-5) | 17/13 (-8.33/-10.56) |
| PSI | 55 | 439 | 413 | 367 | 330 | 302 |
| PSI | 65 | 471 | 435 | 386 | 368 | 339 |
| PSI | 75 | 489 | 457 | 403 | 381 | 362 |
| °F (°C) | ODT IDT | 57/53 (13.89/11.67) | 47/43 (8.33/6.11) | 37/33 (2.78/0.56) | 27/23 (-2.78/-5) | 17/13 (-8.33/-10.56) |
| MPA | 55 | 3.03 | 2.85 | 2.53 | 2.28 | 2.08 |
| MPA | 65 | 3.25 | 3.00 | 2.66 | 2.54 | 2.33 |
| MPA | 75 | 3.38 | 3.15 | 2.78 | 2.63 | 2.49 |