INDOOR UNITS

Outdoor unit Service Manual

ODMI-C1-1407

Revision A: 11MMI-C-1407

Model Numbers:

MS11M-09HRFN1-MW0W

MS11M-12HRFN1-MV0WMS11M-09HRFN1-MX4W

MS11M-18HRFN1-MU0WMS11M-12HRFN1-MW0W

Table of Contents

- Precaution

- Product Description And Label

- Dimension of indoor unit

- Operation Characteristics

- Electronic function

- Wiring Diagrams

- Trouble Shooting

- Disassembly instructions

- Exploded view

WARNING

- Installation MUST conform with local building codes or, in the absence of local codes, with the National Electrical Code NFPA70/ANSI C1-1993 or current edition and Canadian Electrical Code Part1 CSA C.22.1.

- The information contained in the manual is intended for use by a qualified service technician familiar with safety procedures and equipped with the proper tools and test instruments

- Installation or repairs made by unqualified persons can result in hazards to you and others.

- Failure to carefully read and follow all instructions in this manual can result in equipment malfunction, property damage, personal injury and/or death.

CONTENTS

4.	Precaution	2

	1.1 Safety Precaution	2

	1.2 Warning	2

2.	Product Description And Label	6

3.	Dimension of indoor unit	7

Dimension	7

4.	Operation Characteristics	9

5.	Electronic Function	9

5.1 Abbreviation	9

5.2 Main Protection	9

5.3 Operation Modes and Functions	9

6.	Wiring Diagrams	14

7.	Troubleshooting	15

7.1 Display Function	15

7.2 Indoor Unit Error Display	16

7.3 Outdoor Unit Error Display	17

7.4 Diagnosis and Solution	18

7.5 Trouble Criterion Of Main Parts.	64

8.	Disassembly Instructions	75

9.	Exploded View	79

# Precaution

## 1.1 Safety Precaution

- To prevent injury to the user or other people and property damage, the following instructions must be followed.

- Incorrect operation due to ignoring instruction will cause harm or damage.

- Before service unit, be sure to read this service manual at first.

## 1.2 Warning

- Installation

- Do not use a defective or underrated circuit breaker. Use this appliance on a dedicated circuit.

- There is risk of fire or electric shock.

- For electrical work, contact the dealer, seller, a qualified electrician, or an Authorized service center.

- Do not disassemble or repair the product, there is risk of fire or electric shock.

- Always ground the product.

- Install the panel and the cover of control box securely.

- Always install a dedicated circuit and breaker.

- Improper wiring or installation may cause fore or electric shock.

- Use the correctly rated breaker of fuse.

- Do not modify or extend the power cable.

- The unit should be installed, removed, or reinstalled by a certified HVAC professional who is locally licensed to handle this product.

- Be cautious when unpacking and installing the product, sharp edges could cause injury, be especially careful of the edges of the cabinet and the fins on the condenser and evaporator.

- For installation, always contact the dealer or an authorized service center.

- Do not install the product on a defective installation stand as this may cause and accident, injury, or damage to the product.

- Be sure the installation area does not deteriorate with age. If the base collapses, the air conditioner could fall with it, causing property damage, product failure and personal injury.

- Take care to ensure that the power cable could not be disconnected or damaged during operation.

- Do not place anything on the power cable.

- Do not unplug the power supply plug during operation.

- Do not touch (operation) the product with wet hands.

- Do not place a heater or other appliance near the power cable.

- Do not allow water to run into electric parts. It may cause fire, failure of the product, or electric shock.

- Do not store or use flammable gas or combustible near the product.

- Ensure that the condensing unit has proper ventilation.  Do not use the product in a tightly closed space for a long time.

- If smoke is detected during the operation of the unit, discontinue use immediately. Turn the breaker off or disconnect the power supply cable.

- Do not open the inlet grill of the product during operation. (Do not touch the electrostatic filter, if the unit is so equipped.)

- When the product is soaked (flooded or submerged), discontinue use immediately, disconnect the power supply and contact an authorized repair technician or installer.

- Turn the main power off when cleaning or maintaining the product.

- When the product is not be used for a long time, disconnect the power supply or turn off the breaker.

CAUTION

- Always check for gas (refrigerant) leakage after installation or repair of product.

- Low refrigerant levels may cause failure of product.

- Install the drain hose to ensure that water is drained away properly. A bad connection may cause water leakage.

- Keep the product level during installation

- Use two or more people to lift and transport the product.

- Do not install the product where it will be exposed to sea wind (salt spray) directly as this may cause corrosionon the condenser and evaporator fins. Corrosion  could cause product malfunction or inefficient operation.

Operational

- Do not expose the skin directly to cool air for long periods of time. (Do not sit in the draft).

- This could harm to your health.

- Do not use the product for special purposes, such as preserving foods, works of art, etc. It is a consumer air conditioner, not a precision refrigerant system.

- There is risk of damage or loss of property.

- Do not block the inlet or outlet of air flow.

- It may cause product failure.

- Use a soft cloth to clean. Do not use harsh detergents, solvents, etc.

- There is risk of fire, electric shock, or damage to the plastic parts of the product.

- Do not touch the metal parts of the product when removing the air filter. They are very sharp.

- There is risk of personal injury.

- Do not step on or put anything on the product. (outdoor units)

- There is risk of personal injury and failure of product.

- Always insert the filter securely. Clean the filter every two weeks or more often if necessary.

- A dirty filter reduces the efficiency of the air conditioner and could cause product malfunction or damage.

- Do not insert hands or other object through air inlet or outlet while the product is operated.

- There are sharp and moving parts that could cause personal injury.

- Do not drink the water drained from the product.

- It is not sanitary could cause serious health issues.

- Use a firm stool or ladder when cleaning or maintaining the product.

- Be careful and avoid personal injury.

- Replace the all batteries in the remote control with new ones of the same type. Do not mix old and mew batteries or different types of batteries.

- There is risk of fire or explosion.

- Do not recharge or disassemble the batteries. Do not dispose of batteries in a fire.

- They may burn of explode.

- If the liquid from the batteries gets onto your skin or clothes, wash it well with clean water. Do not use the remote of the batteries have leaked.

- The chemical in batteries could cause burns or other health hazards

# Product Description And Label

# Dimension of indoor unit

| Dimension Model | W | H | D |
| --- | --- | --- | --- |
| MS11M-09HRFN1-MW0W | 835mm (32.9in) | 198mm (7.8in) | 280mm (11.0in) |
| MS11M-09HRFN1-MX4W |  |  |  |
| MS11M-12HRFN1-MW0W |  |  |  |
| MS11M-12HRFN1-MV0W |  |  |  |
| MS11M-18HRFN1-MU0W | 990mm (39.0in) | 218mm (8.6in) | 315mm (12.4in) |

| Model | L | R | H | Dimension of installation hole |
| --- | --- | --- | --- | --- |
| MS11M-09HRFN1-MW0W | 140mm (5.5in) | 110mm (4.3in) | 45mm (1.8in) | Φ65mm(2.56in) |
| MS11M-12HRFN1-MV0W |  |  |  |  |
| MS11M-09HRFN1-MX4W |  |  |  |  |
| MS11M-12HRFN1-MW0W |  |  |  |  |

| Model | L(mm) | R(mm) | H(mm) | Dimension of installation hole(mm) |
| --- | --- | --- | --- | --- |
| MS11M-18HRFN1-MU0W | 260mm (10.2in) | 135mm (5.3in) | 45mm (1.8in) | Φ65mm(2.56in) |

# Operation Characteristics

| Temperature Mode | Cooling operation | Heating operation | Drying operation |
| --- | --- | --- | --- |
| Room temperature | 62℉～90℉ | 32℉～86℉ | 62℉～90℉ |
| Outdoor temperature | 32℉～122℉ （5℉～122℉：For the models with low temperature cooling system） | 5℉～76℉ | 32℉～122℉ |

CAUTION:

1. If air conditioner is used beyond the above conditions, the certain protections may action.

2. Room relative humidity should be less than 80%. If the air conditioner operates in excess of this value, the surface of the air conditioner may attract condensation. In this case, please set the vertical air louver to its maximum angle (vertically to the floor), and set the fan to high speed.

# Electronic Function

## 5.1 Abbreviation

T1:  Indoor ambient temperature

T2:  Pipe temperature of indoor heat exchanger

T2B: Coil temperature of indoor heat exchanger outlet.

T3:  Pipe temperature of outdoor heat exchanger

T4:  Outdoor ambient temperature

T5: Compressor discharge temperature

Ts：Setting temp.

## 5.2Main Protection

5.2.1 Three Minutes Delay at restart for compressor.

5.2.2 Fan Speed is out of control.

----When Indoor fan speed keeps too low or too high for certain time, the unit will stop and the LED will display the failure

5.2.3 Indoor fan delayed open function

----When the system starts up, the louver will be active immediately and the indoor fan will open 10s later.

----If the system runs in heating mode, the indoor fan will be also controlled by anti-cold wind function.

## 5.3Operation Modes and Functions

5.3.1 Fan mode.

(1) The outdoor fan and compressor stop.

(2)Temperature setting function is disabled, and no setting temperature is displayed.

(3) Indoor fan can be set to high/med/low/auto.

(4) The louver operates the same as in cooling mode.

(5) Auto fan:

The action of auto fan in fan-only mode is the same as auto fan in cooling mode with 24℃ setting temperature.

5.3.2 Cooling Mode

5.3.2.1 Indoor fan running rules

In cooling mode, indoor fan runs all the time and the speed can be selected as high, medium, low and auto.When the compressor is running, the indoor fan is controlled as below:

Auto fan in cooling mode acts as follow:

5.3.2.4 Evaporator low temperature T2 protection.

When T2<4℃, the indoor has no capacity demand and resume till T2>8℃.

5.3.3 Heating Mode

5.3.3.1 Indoor fan running rules:

Indoor fan speed can be set as high, medium, low and auto fan and the anti-cold-wind function is preferential.If the compressor stops caused by the room temperature rising, the indoor fan will run at super breeze.When the compressor is running, the indoor fan is controlled as below:

Auto fan action in heating mode.

5.3.3.2 High evaporator coil temp.T2 protection:

If T2>63℃, the indoor unit has no capacity demand and resume till 48℃.

5.3.4 Auto-mode

This mode can be chosen by remote controller and the setting temperature can be changed between 17~30℃.

In auto mode, the machine will choose cooling, heating or fan-only mode according to ΔT (ΔT =T1-Ts).

| ΔT=T1-Ts | Running mode |
| --- | --- |
| ΔT＞1℃ | Cooling |
| -1<ΔT≤1℃ | Fan-only |
| ΔT≤-1℃ | Heating |

Indoor fan will run at auto fan of the relevant mode.

The louver operate same as in relevant mode.

If the machine switches mode between heating and cooling, the compressor will keep stopping for 15 minutes and then rechoose mode according to T1-Ts.

If the setting temperature is modified, the machine will rechoose running function.

5.3.5 Dehumidifier mode

5.3.5.1 Indoor fan speed is fixed at breeze and can’t be changed. The louver angle is the same as in cooling mode.

5.3.5.2 Overlow room temperature protection

In dehumidifier mode, if room temperature is lower than 10℃, the indoor fan will stop and not resume until room temperature exceeds 12℃.

5.3.5.3 Evaporator anti-freezing protection is active

5.3.6 Forced operation function

5.3.6.1 Enter forced operation function:

Press the touch button continually, the AC will run as below sequence:

When the machine is off, pressing the touch button will carry the machine to forced auto mode, after this, if pressing the button once again, the machine will turn into forced cooling mode.

In forced cooling mode, pressing touch button will turn off the machine.

5.3.6.2 In forced operation mode, all general protections and remote control are available.

5.3.6.3 Operation rules:

Forced cooling mode:

The indoor fan runs as breeze. After running for 30 minutes, AC will turn to auto mode with 24℃ setting temperature.

Forced auto mode:

The action of forced auto mode is the same as normal auto mode with 24℃ setting temperature.

5.3.6.4 When there’s indoor unit running in forced cooling, it is the master forced cooling unit. Other indoor units will run at forced cooling mode too and they will be the slave forced cooling units. The slave forced cooling units cannot quit forced cooling mode until the master forced cooling unit quit, and turn to cooling mode at low speed with 24℃ setting temperature.

5.3.6.5 The slave forced cooling units will not be controlled by other signals except timer off signal.

5.3.6.6 If AC is running in sleep mode and receives forced operation signal, it will quit the sleep mode.

5.3.7 Timer function

5.3.7.1 Timing range is 24 hours.

5.3.7.2 Timer on.  The machine will turn on automatically when reaching the setting time.

5.3.7.3 Timer off.  The machine will turn off automatically when reaching the setting time.

5.3.7.4 Timer on/off.  The machine will turn on automatically when reaching the setting “on” time, and then turn off automatically when reaching the setting “off” time.

5.3.7.5 Timer off/on.  The machine will turn off automatically when reaching the setting “off” time, and then turn on automatically when reaching the setting “on” time.

5.3.7.6 The timer function will not change the AC current operation mode. Suppose AC is off now, it will not start up firstly after setting the “timer off” function. And when reaching the setting time, the timer LED will be off and the AC running mode has not been changed.

5.3.7.7 The setting time is relative time.

5.3.8 Sleep function mode

5.3.8.1 Operation time in sleep mode is 7 hours. After 7 hours the AC quits this mode and turns off.

5.3.8.2. Operation process in sleep mode is as follow:

When cooling, the setting temperature rises 1℃(be lower than 30℃) every one hour, 2 hours later the setting temperature stops rising and indoor fan is fixed as low speed.

When heating, the setting temperature decreases 1℃(be higher than 17℃) every one hour, 2 hours later the setting temperature stops rising and indoor fan is fixed as low speed.(Anti-cold wind function has the priority)

5.3.8.3 Timer off and remote controller off signals have the priority compared with sleep function.

5.3.8.4 When user uses timer off function in sleep mode(or sleep function in timer off mode), if the timing is less than 7 hours, sleep function will be cancelled when reaching the setting time. If the timing is more than 7 hours, the machine will not stop until reaches the setting time in sleep mode.

5.3.9 Auto-Restart function

The indoor unit is equipped with auto-restart function, which is carried out through an auto-restart module. In case of a sudden power failure, the module memorizes the setting conditions before the power failure. The unit will resume the previous operation setting (not including swing function) automatically after 3 minutes when power returns.

If the memorization condition is forced cooling mode, the unit will run in cooling mode for 30 minutes and turn to auto mode as 24℃ setting temp.

If AC is off before power off and AC is required to start up now, the compressor will have 1 minute delay when power on. Other conditions, the compressor will have 3 minutes delay when restarts.

5.3.10 Follow me

- If the indoor PCB receives the signal which

results from pressing the FOLLOW ME button onremote controller, the buzzer will emit a sound and this indicates the follow me function is initiated. But when the indoor PCB receives signal which sent from remote controller every 3 minutes, the buzzer will not respond. When the unit is running with follow me function, the PCB will control the unit according to the temperature from follow me signal, and the temperature collection function of room temperature sensor will be shielded, but the error detective function of room temperature sensor will be still valid.

- When the follow me function is available,

the PCB will control the unit according to the roomtemperature from the remote controller and the setting temperature.

- The PCB will take action to the mode

change information from remote controller signal, but itwill not affected by the setting temperature.

- When the unit is running with follow me

function, if the PCB doesn’t receive any signal fromremote controller for 7 minutes or pressing FOLLOW ME button again, the follow me function will be turned off automatically, and the temperature will control the unit according to the room temperature detected from its own room temperature sensor and setting temperature.

5.3.11Louver Position Memory Function

When starting the unit again after shutting down, its louver will restore to the angle originally set by the user, but the precondition is that the angle must be within the allowable range, if it exceeds, it will memorize the maximum angle of the louver. During operation, if the power fails or the end user shuts down the unit in the turbo mode, thelouver will restore to the default angle.

5.3.12Ionizer function (optional)

The indoor unit is equipped with Ionizer, which is controlled by the CLEAN AIR button on the remote controller. When the unit is turned on, press the CLEAN AIR button to activate the function. Press it again to stop the function. During the time when Ionizer is controlled by remote controller, Ionizer will be turned off automatically if indoor fan stops running due to malfunctions or anti-cold-wind. When indoor fan restarts after malfunctions being eliminated and anti-cold-wind being released, Ionizer will be available again.

5.3.13 8℃Heating(optional)

In heating operation, the preset temperature of the air conditioner can be as lower as 8℃, which keeps the room temperature steady at 8℃ and prevents household things freezing when the house is unoccupied for a long time in severe cold weather.

# Wiring Diagrams

MS11M-09HRFN1-MW0W,MS11M-09HRFN1-MX4W,MS11M-12HRFN1-MW0W,

MS11M-12HRFN1-MV0W,MS11M-18HRFN1-MU0W

# Troubleshooting

### 7.1 Display Function

|  | ION indication lamp(optional function): This lamp illuminates when Clean Air feature is activated. |
| --- | --- |
|  | DEFROST indication lamp(For cooling & heating models only): Lights up when the air conditioner starts defrosting automatically or when the warm aircontrol feature is activated in heating operation. |
|  | OPERATION indication lamp: This lamp illuminates when the air conditioner is in operation. |
|  | TIMER indication lamp: Lights up during Timer operation. |
|  | Temperature indicator: Displays the temperature settings when the air conditioner is operational. Displays the malfunction code. |

## 7.2Indoor Unit Error Display

| Operation lamp | Timer lamp | Display | LED STATUS | ODU Error |
| --- | --- | --- | --- | --- |
| ★ 1 time | X | E0 | Indoor EEPROM malfunction | —— |
| ★ 2 times | X | E1 | Communication malfunction between indoor and outdoor units | E2 |
| ★4 times | X | E3 | Indoor fanspeed malfunction. | —— |
| ★ 5 times | X | E4 | Indoor room temperature sensor open or short circuit. | —— |
| ★ 6 times | X | E5 | Evaporator coil temperature sensor open or short circuit. | —— |
| ★2 times |  | F1 | Outdoor temperature sensor open or short circuit. | E4 |
| ★3 times |  | F2 | Condenser coil temperature sensor open or short circuit. | E4 |
| ★4 times |  | F3 | Compressor discharge pipe sensoropenor short circuit. | E4 |
| ★5 times |  | F4 | OutdoorEEPROM malfunction | E0 |
| ★6 times |  | F5 | Outdoor fan has been out of control | E8 |
| ★7 times |  | F6 | Indoor unit coil outlet temp. sensor open or short circuit. | E4 |
| ★1 times | ★ | P0 | Inverter module (IPM) malfunction or IGBT over-strong current protection | P6 |
| ★2 times | ★ | P1 | Voltage(High voltage or low voltage ) protection. | E5 |
| ★3 times | ★ | P2 | High temperature protection of compressor top (only for M3OD-27HRDN1-M) | P0 |
| ★5 times | ★ | P4 | Compressor drive error | —— |
| ★6 times | ★ | P5 | Mode conflict | —— |
| ★ flash, light, X extinguished |  |  |  |  |

## 7.3Outdoor Unit Error Display

For M2OC-18HFN1-M,M3OD-27HRDN1-M,M3OC-30HRFN1-M,M4OC-36HRFN1-M

| Display | LED STATUS | IDU Error (Vertu/Luna) | IDU Error (Oasis) | IDU Error (A5 Duct) |
| --- | --- | --- | --- | --- |
| E0 | Outdoor EEPROM malfunction | E5 | F4 | E6 |
| E2 | Communication malfunction between indoor and outdoor units | E1 | E1 | E2 |
| E3 | Communication malfunction between IPM board and outdoor main board | —— | —— | —— |
| E4 | Open or short circuit of outdoor temperature sensor(T3、T4、T5、T2B) | E5 | F2 | E6 |
| E5 | Voltage protection | P1 | P1 | P0 |
| E6 | PFC module protection(Only for M4OC-36HRFN1-M) | —— | —— | —— |
| E8 | Outdoor fan speed has been out of control(Only for DC fan motor models) | —— | F5 | —— |
| F1 | No A Indoor unit coil outlet temp. sensor or connector of sensor is defective | —— | —— | —— |
| F2 | No B Indoor unit coil outlet temp. sensor or connector of sensor is defective | —— | —— | —— |
| F3 | No C Indoor unit coil outlet temp. sensor or connector of sensor is defective | —— | —— | —— |
| F4 | No D Indoor unit coil outlet temp. sensor or connector of sensor is defective | —— | —— | —— |
| P0 | Temperature protection of compressor top (Only for M3OD-27HRDN1-M) | P2 | P2 | P3 |
| P1 | High pressure protection (Only for M4OC-36HRFN1-M) | —— | —— | —— |
| P2 | Low pressure protection(Only for M4OC-36HRFN1-M) | —— | —— | —— |
| P3 | Current protection of compressor | —— | —— | —— |
| P4 | Temperature protection of compressor discharge | —— | —— | —— |
| P5 | High temperature protection of condenser | —— | —— | —— |
| P6 | IPM module protection | P0 | P0 | E5 |

## 7.4Diagnosis and Solution

7.4.1 Indoor unittrouble shooting

7.4.1.1 E0/F4(Indoor EEPROM malfunction) error diagnosis and solution

| Error Code | E0 /F4 |
| --- | --- |
| Malfunction decision conditions | Indoor or outdoor PCB main chip does not receive feedback from EEPROM chip. |
| Supposed causes | - Installation mistake - PCB faulty |

Trouble shooting:

EEPROM: a read-only memory whose contents can be erased and reprogrammed using a pulsed voltage. For the location of EEPROM chip, please refer to the below photos.

Indoor PCB

Outdoor PCB

7.4.1.2 E1(Communication malfunction between indoor and outdoor units) error diagnosis and solution.

| Error Code | E1 |
| --- | --- |
| Malfunction decision conditions | Indoor unit does not receive the feedback from outdoor unit during 120 seconds. |
| Supposed causes | - Wiring mistake - Indoor or outdoor PCB faulty |

Trouble shooting:

Pic 1:Use a multimeter to test the DC voltage between L2 port and S port of outdoor unit. The red pin of multimeter connects with L2 port while the black pin is for S port.

When AC is normal running, the voltage will move alternately between positive value and negative value.

Self-Check OK

Power (some modles)

Operating

els)

Pic 2: :IPM(for dual/tri/qua-zone)

PIC3 :Main board LED when power on and unit standby.

PIC 4: Check point button, press 1 time for check how many indoor units are connected.(for M2OC-18HFN1-M,M3OD-27HRDN1-M,M3OC-30HRFN1-M,M4OC-36HRFN1-M)

Check point button, press 18times for check how many indoor units are connected.(for M2OC-18HRDN1-M,M3OC-27HRDN1-M,M4OC-36HRDN1-M)

7.4.1.3E3(indoor fan speed has been out of control) diagnosis and solution.

F5(Outdoor fan speed has been out of control) diagnosis and solution

| Error Code | E3/F5 |
| --- | --- |
| Malfunction decision conditions | When indoor fan speed keeps too low (300RPM) for certain time, the unit will stop and the LED will display the failure. |
| Supposed causes | - Wiring mistake - Fan ass’y faulty - Fan motor faulty - PCB faulty |

Trouble shooting:

Index 1:

1:Indooror outdoorDC Fan Motor(control chip is in fan motor)

Power on and when the unit is in standby, measure the voltage of pin1-pin3, pin4-pin3 in fan motor connector. If the value of the voltage is not in the range showing in below table, the PCB must has problems and need to be replaced.

DC motor voltage input and output

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | Vs/Vm | 200~380V |
| 2 | --- | --- | --- |
| 3 | Black | GND | 0V |
| 4 | White | Vcc | 13.5~16.5V |
| 5 | Yellow | Vsp | 0~6.5V |
| 6 | Blue | FG | 13.5~16.5V |

7.4.1.4F1/F2/F3/F6(open or short circuit of temperature sensor(T3、T4、T5、T2B)) diagnosis and solution

E4/E5 (open or short circuit of temperature sensor(T1、T2)) diagnosis and solution.

| Error Code | E4/E5/F1/F2/F3/F6 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is lower than 0.06V or higher than 4.94V, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Sensor faulty - PCB faulty |

Trouble shooting:

7.4.1.5P0(IPM module) diagnosis and solution.

| Error Code | P6 |
| --- | --- |
| Malfunction decision conditions | When the voltage signal that IPM send to compressor drive chip is abnormal, the display LED will show “P0” and AC will turn off. |
| Supposed causes | - Wiring mistake - IPM malfunction - Outdoor fan ass’y faulty - Compressor malfunction - Outdoor PCB faulty |

Trouble shooting:

7.4.1.6P1(over voltage or too low voltage protection) diagnosis and solution.

7.4.1.7P2( temperature protection of compressor top) diagnosis and solution.

| Error Code | P2 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is not 5V, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Over load protector faulty - System block - Outdoor PCB faulty |

7.4.1.8P4 Inverter compressor drive error diagnosis and solution

# The trouble shooting is same with one of IPM module protection(P0).

7.4.1.9P5:  Mode conflict.

| Error Code | P5 |
| --- | --- |
| Malfunction decision conditions | The indoor units cannot work cooling mode and heating at same time. Heating mode has a priority. |
| Unit action | - Suppose Indoor unit A working in cooling mode or fan mode, and indoor unit B is set to heating mode, then A will change to off and B will work in heating mode. - Suppose Indoor unit A working in heating mode, and indoor unit B is set to cooling mode or fan mode, then B will change to stand by and A will be no change. |

|  | Cooling mode | Heating Mode | Fan | Off |
| --- | --- | --- | --- | --- |
| Cooling mode | No | Yes | No | No |
| Heating Mode | Yes | No | Yes | No |
| Fan | No | Yes | No | No |
| Off | No | No | No | No |

No: No mode conflict;

Yes: Mode conflict

7.4.2 Outdoor unit trouble shooting (For M2OC-18HFN1-M,M2OD-18HFN1-M,M3OD-27HRDN1-M,M3OC-30HRFN1-M,M4OC-36HRFN1-M)

7.4.2.1 E0(Outdoor EEPROM malfunction) error diagnosis and solution

| Error Code | E0 |
| --- | --- |
| Malfunction decision conditions | PCB main chip does not receive feedback from EEPROM chip |
| Supposed causes | - Installation mistake - PCB faulty |

Trouble shooting:

EEPROM: a read-only memory whose contents can be erased and reprogrammed using a pulsed voltage. For the location of EEPROM chip, please refer to the below photos.

Outdoor PCB(M3OC-30HRFN1-M)

7.4.2.2E2(Communication malfunction between indoor and outdoor units) error diagnosis and solution.

| Error Code | E2 |
| --- | --- |
| Malfunction decision conditions | Indoor unit does not receive the feedback from outdoor unit during 120 seconds or outdoor unit does not receive the feedback from any one indoor unit during 180 seconds. |
| Supposed causes | - Wiring mistake - Indoor or outdoor PCB faulty |

Trouble shooting:

Pic 1:Use a multimeter to test the DC voltage between L2 port and S port of outdoor unit. The red pin of multimeter connects with L2 port while the black pin is for S port.

When AC is normal running, the voltage will move alternately between positive value and negative value.

Pic 2: :IPM(For dual/tri-zone)

Self-Check

Operating

els)

Self-Check

Power,

Operating

els)

Pic 2: :IPM(For qua-zone)

PIC3 :Main board LED when power on and unit standby.

PIC 4: Check point button, press 1 time for check how many indoor units are connected.

7.4.2.3 E3(Communication malfunction between IPM board and outdoor main board) error diagnosis and .

| Error Code | E3 |
| --- | --- |
| Malfunction decision conditions | PCB main chip does not receive feedback from IPM module during 60 seconds. |
| Supposed causes | - Wiring mistake - PCB faulty |

Trouble shooting:

Remark:

Use a multimeter to test the DC voltage between black pin and whitepin of signal wire The normal value should be around 5V.

Use a multimeter to test the DC voltage between blackpin and red pin of signal wire. The normal value should be around 12V.

7.4.2.4E4(open or short circuit of outdoor temperature sensor) diagnosis and solution

F1/F2/F3/F4/F5 (open or short circuit of  indoor coil temperature sensor) diagnosis and solution.

.

| Error Code | E4/F1/F2/F3/F4/F5 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is lower than 0.06V or higher than 4.94V, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Sensor faulty - PCB faulty |

Trouble shooting:

7.4.2.5 E5(Voltage protection) error diagnosis and solution.

| Error Code | E5 |
| --- | --- |
| Malfunction decision conditions | An abnormal voltage rise or drop is detected by checking the specified voltage detection circuit. |
| Supposed causes | - Power supply problems. - System leakage or block - PCB faulty |

Trouble shooting:

IPM (for dual/tri-zone)

IPM (for qua-zone)

P-N (for dual/tri-zone)

P-N (for qua-zone)

bridge rectifier(for dual/tri-zone)

bridge rectifier(for qua-zone)

Remark:

Measure the DC voltage between + and - port. The normal value should be 190V~250V.

7.4.2.6 E6(PFC module protection) error diagnosis and solution. (Only for M4OC-36HRFN1-M)

| Error Code | E6 |
| --- | --- |
| Malfunction decision conditions | When the voltage signal that PFC sends to main control board is abnormal, the display LED will show “E6” and AC will turn off. |
| Supposed causes | - Wiring mistake - Outdoor PCB faulty - Inductance of PFC module faulty - PFC module malfunction |

Trouble shooting:

Inductance

Two ports of the inductance

7.4.2.7E8(Outdoor fan speed has been out of control) diagnosis and solution(Only for DC fan motor models).

| Error Code | E8 |
| --- | --- |
| Malfunction decision conditions | When outdoor fan speed keeps too low (300RPM) or too high(2400RPM) for certain time, the unit will stop and the LED will display the failure. |
| Supposed causes | - Wiring mistake - Fan ass’y faulty - Fan motor faulty - PCB faulty |

Trouble shooting:

Index 1:

1.  DC fan motor(control chip is inside fan motor)

Power on and when the unit is in standby, measure the voltage of pin1-pin3, pin4-pin3 in fan motor connector. If the value of the voltage is not in the range showing in below table, the PCB must have problems and need to be replaced.

DC motor voltage input and output

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | Vs/Vm | 200~380V |
| 2 | --- | --- | --- |
| 3 | Black | GND | 0V |
| 4 | White | Vcc | 13.5~16.5V |
| 5 | Yellow | Vsp | 0~6.5V |
| 6 | Blue | FG | 13.5~16.5V |

Vcc

Vs

FG

Vsp

7.4.2.8 P0(Temperature protection of compressor top) error diagnosis and solution. (Only for M3OD-27HRDN1-M)

| Error Code | P0 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is not 5V, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Over load protector faulty - System block - Outdoor PCB faulty |

Trouble shooting:

7.4.2.9P1(High pressure protection) error diagnosis and solution. (Only for M4OC-36HRFN1-M)

| Error Code | P1 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is not 5V, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Over load protector faulty - System block - Outdoor PCB faulty |

Trouble shooting:

7.4.2.10P2(Low pressure protection) error diagnosis and solution. (Only for M4OC-36HRFN1-M)

| Error Code | P2 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is not 5V, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Over load protector faulty - System block - Outdoor PCB faulty |

Trouble shooting:

7.4.2.11P3(Current protection of compressor) error diagnosis and solution.

| Error Code | P3 |
| --- | --- |
| Malfunction decision conditions | If the outdoor current exceeds the current limit value, the LED will display the failure. |
| Supposed causes | - Wiring mistake - Over load protector faulty - System block - Outdoor PCB faulty |

Trouble shooting:

7.4.2.12P4(Temperature protection of compressor discharge) error diagnosis and solution.

| Error Code | P4 |
| --- | --- |
| Malfunction decision conditions | When the compressor discharge temperature(T5) is more than 115℃ for 10 seconds, the compressor will stop and restart till T5 is less than 90℃. |
| Supposed causes | - Refrigerant leakage - Wiring mistake - The discharge temperature sensor faulty - Outdoor PCB faulty |

Trouble shooting:

7.4.2.13P5(High temperature protection of condenser) error diagnosis and solution.

| Error Code | P5 |
| --- | --- |
| Malfunction decision conditions | When outdoor pipe temperature is more than 65°C, the unit will stop, and unit runs again when outdoor pipe temperature is less than 52°C |
| Supposed causes | - The condenser temperature sensor faulty - Heat exchanger dirty - System block |

Trouble shooting:

7.4.2.14P6(IPM module protection) error diagnosis and solution.

| Error Code | P6 |
| --- | --- |
| Malfunction decision conditions | When the voltage signal that IPM send to compressor drive chip is abnormal, the display LED will show “P6” and AC will turn off. |
| Supposed causes | - Wiring mistake - IPM malfunction - Outdoor fan ass’y faulty - Compressor malfunction - Outdoor PCB faulty |

Trouble shooting:

## 7.5 Trouble Criterion Of Main Parts.

Spec.

| Indoor unit |  |  |  |  |
| --- | --- | --- | --- | --- |
| Model | MS11M-09HRFN1-MW0W | MS11M-12HRFN1-MV0W | MS11M-18HRFN1-MU0W | MS11M-09HRFN1-MX4W |
| Indoor fan motor | WZDK20-38G | WZDK20-38G | WZDK58-38G | WZDK20-38G |
| Model | MS11M-12HRFN1-MW0W |  |  |  |
| Indoor fan motor | WZDK20-38G |  |  |  |
| Outdoor unit |  |  |  |  |
| Model | M2OC-18HFN1-M | M3OD-27HRDN1-M | M3OC-30HRFN1-M | M4OC-36HRFN1-M |
| Compressor | DA130S1C-20FZ | DA150S1C-20FZ | DA250S2C-30MT | TNB306FPGMC-L |
| Outdoor fan motor | WZDK50-38G | YDK53-6FB(B) | WZDK72-38G | WZDK180-38G |

1.Temperature sensor checking

Disconnect the temperature sensor from PCB, measure the resistance value with a tester.

Temperature Sensors.

Room temp.(T1) sensor,

Indoor coil temp.(T2) sensor,

Outdoor coil temp.(T3) sensor,

Outdoor ambient temp.(T4) sensor,

Compressor discharge temp.(T5) sensor.

Measure the resistance value of each winding by using the multi-meter.

Appendix 1 Temperature Sensor Resistance Value Table  (℃--K)

| ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm |
| --- | --- | --- | --- | --- | --- | --- | --- |
| -20 | 115.266 | 20 | 12.6431 | 60 | 2.35774 | 100 | 0.62973 |
| -19 | 108.146 | 21 | 12.0561 | 61 | 2.27249 | 101 | 0.61148 |
| -18 | 101.517 | 22 | 11.5000 | 62 | 2.19073 | 102 | 0.59386 |
| -17 | 96.3423 | 23 | 10.9731 | 63 | 2.11241 | 103 | 0.57683 |
| -16 | 89.5865 | 24 | 10.4736 | 64 | 2.03732 | 104 | 0.56038 |
| -15 | 84.2190 | 25 | 10.000 | 65 | 1.96532 | 105 | 0.54448 |
| -14 | 79.3110 | 26 | 9.55074 | 66 | 1.89627 | 106 | 0.52912 |
| -13 | 74.5360 | 27 | 9.12445 | 67 | 1.83003 | 107 | 0.51426 |
| -12 | 70.1698 | 28 | 8.71983 | 68 | 1.76647 | 108 | 0.49989 |
| -11 | 66.0898 | 29 | 8.33566 | 69 | 1.70547 | 109 | 0.48600 |
| -10 | 62.2756 | 30 | 7.97078 | 70 | 1.64691 | 110 | 0.47256 |
| -9 | 58.7079 | 31 | 7.62411 | 71 | 1.59068 | 111 | 0.45957 |
| -8 | 56.3694 | 32 | 7.29464 | 72 | 1.53668 | 112 | 0.44699 |
| -7 | 52.2438 | 33 | 6.98142 | 73 | 1.48481 | 113 | 0.43482 |
| -6 | 49.3161 | 34 | 6.68355 | 74 | 1.43498 | 114 | 0.42304 |
| -5 | 46.5725 | 35 | 6.40021 | 75 | 1.38703 | 115 | 0.41164 |
| -4 | 44.0000 | 36 | 6.13059 | 76 | 1.34105 | 116 | 0.40060 |
| -3 | 41.5878 | 37 | 5.87359 | 77 | 1.29078 | 117 | 0.38991 |
| -2 | 39.8239 | 38 | 5.62961 | 78 | 1.25423 | 118 | 0.37956 |
| -1 | 37.1988 | 39 | 5.39689 | 79 | 1.21330 | 119 | 0.36954 |
| 0 | 35.2024 | 40 | 5.17519 | 80 | 1.17393 | 120 | 0.35982 |
| 1 | 33.3269 | 41 | 4.96392 | 81 | 1.13604 | 121 | 0.35042 |
| 2 | 31.5635 | 42 | 4.76253 | 82 | 1.09958 | 122 | 0.3413 |
| 3 | 29.9058 | 43 | 4.57050 | 83 | 1.06448 | 123 | 0.33246 |
| 4 | 28.3459 | 44 | 4.38736 | 84 | 1.03069 | 124 | 0.32390 |
| 5 | 26.8778 | 45 | 4.21263 | 85 | 0.99815 | 125 | 0.31559 |
| 6 | 25.4954 | 46 | 4.04589 | 86 | 0.96681 | 126 | 0.30754 |
| 7 | 24.1932 | 47 | 3.88673 | 87 | 0.93662 | 127 | 0.29974 |
| 8 | 22.5662 | 48 | 3.73476 | 88 | 0.90753 | 128 | 0.29216 |
| 9 | 21.8094 | 49 | 3.58962 | 89 | 0.87950 | 129 | 0.28482 |
| 10 | 20.7184 | 50 | 3.45097 | 90 | 0.85248 | 130 | 0.27770 |
| 11 | 19.6891 | 51 | 3.31847 | 91 | 0.82643 | 131 | 0.27078 |
| 12 | 18.7177 | 52 | 3.19183 | 92 | 0.80132 | 132 | 0.26408 |
| 13 | 17.8005 | 53 | 3.07075 | 93 | 0.77709 | 133 | 0.25757 |
| 14 | 16.9341 | 54 | 2.95896 | 94 | 0.75373 | 134 | 0.25125 |
| 15 | 16.1156 | 55 | 2.84421 | 95 | 0.73119 | 135 | 0.24512 |
| 16 | 15.3418 | 56 | 2.73823 | 96 | 0.70944 | 136 | 0.23916 |
| 17 | 14.6181 | 57 | 2.63682 | 97 | 0.68844 | 137 | 0.23338 |
| 18 | 13.9180 | 58 | 2.53973 | 98 | 0.66818 | 138 | 0.22776 |
| 19 | 13.2631 | 59 | 2.44677 | 99 | 0.64862 | 139 | 0.22231 |

Appendix 2

| Unit: ℃---K Discharge temp. sensor table |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| -20 | 542.7 | 20 | 68.66 | 60 | 13.59 | 100 | 3.702 |
| -19 | 511.9 | 21 | 65.62 | 61 | 13.11 | 101 | 3.595 |
| -18 | 483 | 22 | 62.73 | 62 | 12.65 | 102 | 3.492 |
| -17 | 455.9 | 23 | 59.98 | 63 | 12.21 | 103 | 3.392 |
| -16 | 430.5 | 24 | 57.37 | 64 | 11.79 | 104 | 3.296 |
| -15 | 406.7 | 25 | 54.89 | 65 | 11.38 | 105 | 3.203 |
| -14 | 384.3 | 26 | 52.53 | 66 | 10.99 | 106 | 3.113 |
| -13 | 363.3 | 27 | 50.28 | 67 | 10.61 | 107 | 3.025 |
| -12 | 343.6 | 28 | 48.14 | 68 | 10.25 | 108 | 2.941 |
| -11 | 325.1 | 29 | 46.11 | 69 | 9.902 | 109 | 2.86 |
| -10 | 307.7 | 30 | 44.17 | 70 | 9.569 | 110 | 2.781 |
| -9 | 291.3 | 31 | 42.33 | 71 | 9.248 | 111 | 2.704 |
| -8 | 275.9 | 32 | 40.57 | 72 | 8.94 | 112 | 2.63 |
| -7 | 261.4 | 33 | 38.89 | 73 | 8.643 | 113 | 2.559 |
| -6 | 247.8 | 34 | 37.3 | 74 | 8.358 | 114 | 2.489 |
| -5 | 234.9 | 35 | 35.78 | 75 | 8.084 | 115 | 2.422 |
| -4 | 222.8 | 36 | 34.32 | 76 | 7.82 | 116 | 2.357 |
| -3 | 211.4 | 37 | 32.94 | 77 | 7.566 | 117 | 2.294 |
| -2 | 200.7 | 38 | 31.62 | 78 | 7.321 | 118 | 2.233 |
| -1 | 190.5 | 39 | 30.36 | 79 | 7.086 | 119 | 2.174 |
| 0 | 180.9 | 40 | 29.15 | 80 | 6.859 | 120 | 2.117 |
| 1 | 171.9 | 41 | 28 | 81 | 6.641 | 121 | 2.061 |
| 2 | 163.3 | 42 | 26.9 | 82 | 6.43 | 122 | 2.007 |
| 3 | 155.2 | 43 | 25.86 | 83 | 6.228 | 123 | 1.955 |
| 4 | 147.6 | 44 | 24.85 | 84 | 6.033 | 124 | 1.905 |
| 5 | 140.4 | 45 | 23.89 | 85 | 5.844 | 125 | 1.856 |
| 6 | 133.5 | 46 | 22.89 | 86 | 5.663 | 126 | 1.808 |
| 7 | 127.1 | 47 | 22.1 | 87 | 5.488 | 127 | 1.762 |
| 8 | 121 | 48 | 21.26 | 88 | 5.32 | 128 | 1.717 |
| 9 | 115.2 | 49 | 20.46 | 89 | 5.157 | 129 | 1.674 |
| 10 | 109.8 | 50 | 19.69 | 90 | 5 | 130 | 1.632 |
| 11 | 104.6 | 51 | 18.96 | 91 | 4.849 |  |  |
| 12 | 99.69 | 52 | 18.26 | 92 | 4.703 |  |  |
| 13 | 95.05 | 53 | 17.58 | 93 | 4.562 |  |  |
| 14 | 90.66 | 54 | 16.94 | 94 | 4.426 |  |  |
| 15 | 86.49 | 55 | 16.32 | 95 | 4.294 | B(25/50)=3950K |  |
| 16 | 82.54 | 56 | 15.73 | 96 | 4.167 |  |  |
| 17 | 78.79 | 57 | 15.16 | 97 | 4.045 | R(90℃)=5KΩ±3% |  |
| 18 | 75.24 | 58 | 14.62 | 98 | 3.927 |  |  |
| 19 | 71.86 | 59 | 14.09 | 99 | 3.812 |  |  |

Appendix 3:

| ℃ | 10 11 12 13 14 15 16 17 18 19 20 21 22 |
| --- | --- |
| ℉ | 48 50 52 54 56 58 60 62 64 66 68 70 72 |
| ℃ | 23 24 25 26 27 28 29 30 31 32 33 34 35 |
| ℉ | 74 76 78 80 82 84 86 88 90 92 94 96 98 |

2.Compressor check

Measure the resistance value of each winding by using the tester.

| Position |  | Resistance Value |  |  |
| --- | --- | --- | --- | --- |
|  | DA130S1C-20FZ | DA150S1C-20FZ | DA250S2C-30MT | TNB306FPGMC-L |
| Blue - Red | 0.95Ω(20℃) | 0.95Ω(20℃) | 0.55Ω(20℃) | 0.53Ω(20℃) |

3.IPM continuity check

Turn off the power, let the large capacity electrolytic capacitors discharge completely, and dismount the IPM. Use a digital tester to measure the resistance between P and UVWN; UVW and N.

| Digital tester |  | Normal resistance value | Digital tester |  | Normal resistance value |
| --- | --- | --- | --- | --- | --- |
| (+)Red | (-)Black | ∞ (Several MΩ) | (+)Red | (-)Black | ∞ (Several MΩ) |
| P | N |  | U | N |  |
|  | U |  | V |  |  |
|  | V |  | W |  |  |
|  | W |  | (+)Red |  |  |

4. AC Fan Motor.

Measure the resistance value of each winding by using the tester.

| Position | Resistance Value |  |  |  |
| --- | --- | --- | --- | --- |
|  | RPG20B |  | RPG28H |  |
| Black - Red | 381Ω±8% (20℃) (Brand: Weiling) | 342Ω±8% (20℃) (Brand: Dayang) | 183.6Ω±8% (20℃) (Brand: Weiling) | 180Ω±8% (20℃) (Brand: Wolong) |
| White - Black | 267Ω±8% (20℃) (Brand: Weiling) | 253Ω±8% (20℃) (Brand: Dayang) | 206Ω±8% (20℃) (Brand: Weiling) | 190Ω±8% (20℃) (Brand: Wolong) |

Measure the resistance value of each winding by using the tester.

| Position | Resistance Value |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | YDK70-6FB | YDK180-8GB | YSK27-4G | YSK68-4B | YDK45-6B | YSK25-6L | YDK53-6FB(B) |
| Black - Red | 56Ω±8% (20℃) | 24.5Ω±8% (20℃) | 317Ω±8% (20℃) | 145Ω±8% (20℃) | 345Ω±8% (20℃) | 627Ω±8% (20℃) | 88.5Ω±8% (20℃) |
| Red - Yellow | 76Ω±8% (20℃) | 19Ω±8% (20℃) | 252Ω±8% (20℃) | 88Ω±8% (20℃) | 150Ω±8% (20℃) | 374.3Ω±8% (20℃) | 138Ω±8% (20℃) |
| Yellow - Blue | 76Ω±8% (20℃) | 19Ω±8% (20℃) | 252Ω±8% (20℃) | 88Ω±8% (20℃) | 150Ω±8% (20℃) | 374.3Ω±8% (20℃) | 138Ω±8% (20℃) |

5.4-way valve

1.Power on,use a digital tester to measure the voltage, when the unit operates in cooling, it is 0V. When the unit operates in heating, it is about 230VAC.

If the value of the voltage is not in the range, the PCB must have problems and need to be replaced.

2 Turn off the power, use a digital tester to measure the resistance. The value should be 1.8~2.5 KΩ.

6.EXV check

Disconnect  the connectors.

6         5         4        3        2         1

Red  BrownBlue  Orange Yellow White

Resistance to EXV coil

| Color of lead wire | Normal Value |
| --- | --- |
| Red- Blue | About 50Ω |
| Red - Yellow |  |
| Brown-Orange |  |
| Brown-White |  |

Red - Yellow

Red- Blue

Brown-Orange

Brown-White

# Disassembly Instructions

| No. | Parts name | Procedures | Remarks |
| --- | --- | --- | --- |
| 1 | Front panel | How to remove the front panel. - Pull the below side of the panel and release the clips. Then remove the front panel. Clip Remove the filter and horizontal louver. - Remove the four fixing screws. - Remove the cover (one screw). - Lift the panel frame and release the connector of display ass’y. connectors. Then remove the panel frame assembly. | Overview: One screw fixing the cover Panel Filter Clip Four screws Connector for display ass’y |
| 2 | Electrical parts | How to remove the electrical parts. Swing motor After remove the frontpanel from procedure 1, pull out the roomtemp. sensor and evaporator coil sensor. Remove the grounding screws. - Pull out the clip toward the left side and open the cover. - Remove the fixing screw and open the electrical box cover. . - Pull out the connectors of the swing motor and fan motor . - Remove the fixing screw and then remove the electronic control box and air outlet ass’y. | Room temp. sensor Grounding screws Clip for electronic control box cover Evaporatorcoil temp. sensor Fan motor connector and swing motor connector Fixing screw |
| 3 | Evaporator | How to remove the evaporator. - After remove the front panelass’y and electrical parts following procedure 1 and procedure 2, remove the pipeholder at the rear side of the unit. - Remove the two screws onthe evaporator at the base bearing side. - Remove two screws onthe evaporator at the fixed plates and then lift the evaporatorass’y. | Two screws at the base bearing side Two screws at the fixed plates |
| 4 | Fan and motor | How to remove the fan and motor. - After remove the evaporator ass’y following procedure 1, procedure 2 and procedure 3, remove the three screws fixing the cover - Remove the screw fixing the motor and then pull out the motor. | Three screws One screw |

# Exploded View

- MS11M-09HRFN1-MW0W:

| No. | Part Name | Qty | BOM Code | No. | Part Name | Qty | BOM Code |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Panel assembly | 1 | 201132590959 | 15 | Horizontal louver | 1 | 201132590956 |
| 2 | Air filter | 2 | 201132590962 | 16 | Chassis assembly | 1 | 201132590963 |
| 3 | Display box assembly | 1 | 203332390972 | 16.1 | Louver motor | 1 | 202400200031 |
| 3.1 | Display board assembly | 1 | 201332391249 | 17 | Pipe clamp board | 1 | 201119900949 |
| 4 | Cover of indoor electronic control box | 1 | 201119900948 | 18 | Installation plate | 1 | 201232590037 |
| 5 | Panel frame assembly | 1 | 201132590958 | 19 | Electronic control box assembly | 1 | 203332391073 |
| 5.1 | Screw cap | 2 | 201119900950 | 19.1 | Electronic control box I | 1 | 201132490125 |
| 6 | Drain hose | 1 | 201101020038 | 19.2 | Electronic control box II | 1 | 201132490139 |
| 7 | Pipe nut | 1 | 201600330002 | 19.3 | Main control board assembly | 1 | 201332391485 |
| 7 | Pipe nut | 1 | 201600330001 | 19.4 | Ambient temperature sensor assembly | 1 | 202433190000 |
| 8 | Fix clamp of temperature sensor | 1 | 201102000305 | 19.5 | Pipe temperature sensor assembly | 1 | 202301300584 |
| 9 | Evaporator assembly | 1 | 201532590453 | 19.6 | Wire joint | 1 | 202301450119 |
| 10 | Fan motor cover | 1 | 201132490127 | 20 | Cover of electronic control box | 1 | 201132490126 |
| 11 | Asynchronous motor | 1 | 202400370022 | 21 | Remote Controller | 1 | 203355091532 |
| 12 | Bearing holder | 1 | 201119900952 | 22 | Seal | 1 | 202720090001 |
| 13 | Bearing base | 1 | 202719900606 | 23 | Drain joint | 1 | 201101020011 |
| 14 | Cross flow fan | 1 | 201100200054 | 24 | Air freshening filter | 1 | 201131410703 |

- MS11M-12HRFN1-MV0W:

| No. | Part Name | Qty | BOM Code | No. | Part Name | Qty | BOM Code |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Panel assembly | 1 | 201132590959 | 15 | Horizontal louver | 1 | 201132590956 |
| 2 | Air filter | 2 | 201132590962 | 16 | Chassis assembly | 1 | 201132590963 |
| 3 | Display box assembly | 1 | 203332390972 | 16.1 | Louver motor | 1 | 202400200031 |
| 3.1 | Display board assembly | 1 | 201332391249 | 17 | Pipe clamp board | 1 | 201119900949 |
| 4 | Cover of indoor electronic control box | 1 | 201119900948 | 18 | Installation plate | 1 | 201232590037 |
| 5 | Panel frame assembly | 1 | 201132590958 | 19 | Electronic control box assembly | 1 | 203332591105 |
| 5.1 | Screw cap | 2 | 201119900950 | 19.1 | Electronic control box I | 1 | 201132490125 |
| 6 | Drain hose | 1 | 201101020038 | 19.2 | Electronic control box II | 1 | 201132490139 |
| 7 | Pipe nut | 1 | 201600330003 | 19.3 | Main control board assembly | 1 | 201332591013 |
| 7 | Pipe nut | 1 | 201600330001 | 19.4 | Ambient temperature sensor assembly | 1 | 202433190000 |
| 8 | Fix clamp of temperature sensor | 1 | 201102000305 | 19.5 | Pipe temperature sensor assembly | 1 | 202301300584 |
| 9 | Evaporator assembly | 1 | 201532590458 | 19.6 | Wire joint | 1 | 202301450119 |
| 10 | Fan motor cover | 1. | 201132490127 | 20 | Cover of electronic control box | 1 | 201132490126 |
| 11 | Asynchronous motor | 1 | 202400370022 | 21 | Remote Controller | 1 | 203355091532 |
| 12 | Bearing holder | 1 | 201119900952 | 22 | Seal | 1 | 202720090001 |
| 13 | Bearing base | 1 | 202719900606 | 23 | Drain joint | 1 | 201101020011 |
| 14 | Cross flow fan | 1 | 201100200054 | 24 | Air freshening filter | 1 | 201131410703 |

- MS11M-18HRFN1-MU0W:

| No. | Part Name | Qty | BOM Code | No. | Part Name | Qty | BOM Code |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Panel assembly | 1 | 201132890674 | 15 | Bearing holder | 1 | 201119900952 |
| 2 | Air filter | 2 | 201132890670 | 16 | Bearing base | 1 | 202719900606 |
| 3 | Display box assembly | 1 | 203332390972 | 17 | Cross flow fan | 1 | 201100200056 |
| 3.1 | Display board assembly | 1 | 201332391249 | 18 | Chassis assembly | 1 | 201132890703 |
| 4 | Cover of indoor electronic control box | 1 | 201133091048 | 19 | Pipe clamp board | 1 | 201232800103 |
| 5 | Panel frame assembly | 1 | 201132890673 | 20 | Installation plate | 1 | 201232590038 |
| 5.1 | Screw cap | 3 | 201119900950 | 21 | Electronic control box assembly | 1 | 203332890569 |
| 6 | Horizontal louver | 1 | 201132890671 | 21.1 | Wire joint | 1 | 202301450119 |
| 7 | Air outlet assembly | 1 | 201132890677 | 21.2 | Electronic control box | 1 | 201133090976 |
| 7.1 | Louver motor | 1 | 202400200120 | 21.3 | Main control board assembly | 1 | 201332890610 |
| 8 | Drain hose | 1 | 201101020038 | 21.5 | Ambient temperature sensorassembly | 1 | 202432390005 |
| 9 | Pipe nut | 1 | 201600330001 | 21.6 | Pipe temperature sensor assembly | 1 | 202301300584 |
| 9 | Pipe nut | 1 | 201600330003 | 22 | Cover of electronic control box | 1 | 201133090981 |
| 10 | Fix clamp of temperature sensor | 1 | 201102000305 | 23 | Remote Controller | 1 | 203355091532 |
| 11 | Evaporator assembly | 1 | 201532890153 | 24 | Seal | 1 | 202720090001 |
| 12 | Fan motor cover | 1 | 201133090980 | 25 | Drain joint | 1 | 201101020011 |
| 13 | Fixing board of fan motor | 1 | 201133090167 | 26 | Air freshening filter | 1 | 201131410703 |
| 14 | Asynchronous motor | 1 | 202400300064 |  |  |  |  |